# Miami-Date Water and Sewer Department

# Central District Wastewater Treatment Plant

# Facility ID No. 0250476

# Miami-Dade County

# Title V Air Operation Permit Renewal

Permit No. 0250476-015-AV

(Renewal of Title V Air Operation Permit No. Permit No. 0250476-012-AV)

# Permitting Authority:

State of Florida

Department of Environmental Protection

Permitting Program, Northeast District

8800 Baymeadows Way W., Suite 100

Jacksonville, Florida 32256-7590

# Telephone: (904) 256-1700

Email:  DEP_NED@floridadep.gov

# Compliance Authority:

State of Florida

Southeast District Office

3301 Gun Club Road; MSC 7210-1

# West Palm Beach, Florida  33406

Telephone:  (561) 681-6600

Email:  SED.Air@FloridaDEP.gov

Title V Air Operation Permit Renewal

Permit No. 0250476-015-AV

Table of Contents

Section	Page Number

Placard Page 	 1

- Facility Information.

- Facility Description. 	 2

- Summary of Emissions Units. 	 2

- Applicable Regulations. 	 3

- Facility-wide Conditions. 	 4

- Emissions Units and Conditions.

- Five, EMD Diesel Engine Electric Generators (EUs 013, 014, 015, 019, 020)	7

- Four, 1.2 MW Copper-Superior Digester Gas Electric Co-generator units (EUs 021, 022, 024, 025)	 21

- One, 37 hp Diesel Engine Driven Starting Air Compressor (EU 023)	32

- Gasoline Dispensing Facility (EU 27)…………………………………………………………………… 35

- Appendices.

Appendix A, Abbreviations, Acronyms, Citations and Identification Numbers.

Appendix NSPS A, 40 CFR 60 (NSPS), Subpart A – General Provisions.

Appendix NSPS JJJJ, 40 CFR 60 (NSPS), Subpart JJJJ

Appendix NESHAP A, 40 CFR 63 (NESHAP), Subpart A – General Provisions.

Appendix NESHAP ZZZZ, 40 CFR 63 (NESHAP), Subpart ZZZZ

Appendix NESHAP CCCCCC, 40 CFR 63 (NESHAP), Subpart CCCCCC

Appendix I, List of Insignificant Emissions Units and/or Activities.

Appendix RR, Facility-wide Reporting Requirements.

Appendix TR, Facility-wide Testing Requirements.

Appendix TV, Title V General Conditions.

Appendix U, List of Unregulated Emissions Units and/or Activities

Referenced Attachments. ……………………………………………………………………………………..

Figure 1, Summary Report-Gaseous and Opacity Excess Emission and

Monitoring System Performance (40 CFR 60, July, 1996).

Table H, Permit History.

Permittee:	Permit No. 0250476-015-AV

Miami-Dade Water and Sewer Department	Central District Wastewater Treatment Plant

PO Box 330316	Facility ID No. 0250476

Miami, Florida 33233-0316	Title V Air Operation Permit Renewal

The purpose of this permit is to renew the Title V air operation permit for the above referenced facility.  The existing Central District Wastewater Treatment Plant is located in Miami-Dade County at 3869 Rickenbacker Causeway, Miami, Florida.  UTM Coordinates are: Zone 17, 585.19 km East and 2848.09 km North.  Latitude is:  25 44’ 54” North and Longitude:  80 09’ 02” West.

The Title V air operation permit is issued under the provisions of Chapter 403, Florida Statutes (F.S.), and Florida Administrative Code (F.A.C.) Chapters 62-4, 62-210, and 62-213.  The above named permittee is hereby authorized to operate the facility in accordance with the terms and conditions of this permit.

0250476-015-AV Effective Date:  May 11, 2020

Renewal Application Due Date:  September 28, 2024

Expiration Date: 		May 11, 20205

Thomas G. Kallemeyn

Permitting Program Administrator

TGK/rfs

Table of Contents

Subsection A.  Facility Description.

The Central District Wastewater Treatment Plant Cogeneration Facility (CDWWTP) is engaged in wastewater treatment activities and is publicly owned.  The first treatment facilities at the Virginia Key site became operational in 1956 with a capacity of 47 millions of gallons per day (mgd).  Since that time numerous additions and modifications to the plant have been made, including the change from aeration to oxygenation in the original plant.  The facility consists of two parallel wastewater treatment trains: named Plant No. 1 and Plant No. 2.  Plant 1 is rated at 60 mgd annual average daily flow and Plant 2 is rated for 83 mgd annual average daily flow.  The total facility is permitted to treat 143 mgd annual average daily flow.  The liquid process is designated as Emissions Unit (EU) 008 which consists of aerated grit chambers, oxygenation tanks, sludge concentration tanks, secondary clarifiers, and chlorine contact basins.

Electricity for in-plant operations is produced by four nominal 1.2 MW Copper-Superior Digester Gas Electric Co-generator engines (Model 16GTLD) designated as EU021, EU022, EU 024, and EU025.  Backup emergency power is provided by three nominal 2.5 Megawatt (MW) diesel engine-driven electric standby generators (Model EMD 20-645E4B) designated as EU 013, 014, and 015; and two nominal 2.865 MW diesel engine electric standby generators, (Model 20-645F4B) designated as EU 019 and 020.  A 37 HP Diesel Engine, designated as EU 023, is available to provide compressed air to start the emergency generators in the event all electrical power is lost at the facility.  In addition, there are eleven digester gas flares at the facility designated as EU 018.

There is an agreement with the local utility that the facility provide peak shaving or non-emergency demand response, in exchange for financial incentives to the facility.  Because of this agreement, per Federal Rule 40 CFR 63 Subpart ZZZZ, the existing diesel driven standby generators (EU 013, 014, 015, 019 and 020) are considered to be non-emergency engines, and therefore required the installation of oxidation catalysts.  The 37 HP Diesel Engine (EU023) is also regulated by the Federal Regulation 40 CFR 63 Subpart ZZZZ.

Subsection B.  Summary of Emissions Units.

| EU No. | ## Brief Description |
| --- | --- |
| Regulated Emissions Units |  |
| 013 | 2.5 MW Diesel Engine Electric Generator #1 |
| 014 | 2.5 MW Diesel Engine Electric Generator #2 |
| 015 | 2.5 MW Diesel Engine Electric Generator #3 |
| 019 | 2.865 MW Diesel Engine Electric Generator #4 |
| 020 | 2.865 MW Diesel Engine Electric Generator #5 |
| 021 | 1.2 MW Digester Gas Electric Co-generator (#3) |
| 022 | 1.2 MW Digester Gas Electric Co-generator (#4) |
| 023 | 37 HP Emergency Air Compressor Diesel Engine |
| 024 | 1.2 MW Digester Gas Electric Co-generator (#1) |
| 025 | 1.2 MW Digester Gas Electric Co-generator (#2) |
| 027 | Gasoline Dispensing Facility |
| Unregulated Emission Units and/or Activities |  |
| 008 | Wastewater Treatment Plant - Liquid Processes |
| 017 | Wastewater Treatment Plant – Solids Handling Processes |
| 018 | Wastewater Treatment Plant – Digester Gas Flares |

Also, included in this permit are miscellaneous insignificant emissions units and/or activities (see Appendix I, List of Insignificant Emissions Units and/or Activities).

Subsection C.  Applicable Regulations.

Based on the Title V air operation permit renewal application received August 9, 2019, this facility is not a major source of hazardous air pollutants (HAP).  The existing facility is a prevention of significant deterioration (PSD) major source of air pollutants in accordance with Rule 62-212.400, F.A.C.  A summary of applicable regulations is shown in the following table.

| Regulation | ## EU No(s). |
| --- | --- |
| ## Federal Rule Citations |  |
| 40 CFR 60, Subpart A, NSPS General Provisions | 021, 022, 024, 025 |
| 40 CFR 60, Subpart JJJJ, NSPS for Spark Ignition Engines | 021, 022, 024, 025 |
| 40 CFR 63, Subpart A, NESHAP General Provisions | 013, 014, 015, 019, 020, 021, 022, 023, 024, 025, 027 |
| 40 CFR 63, Subpart ZZZZ, NESHAP for Reciprocating Engines | 013, 014, 015, 019, 020, 021,022, 023, 024, 025 |
| 40 CFR 63, Subpart CCCCCC, Gasoline Dispensing Facilities | 027 |
| Section 112(r) of CAA Prevention of Accidental Releases |  |
| State Rule Citations |  |
| 62-4, F.A.C., Permits |  |
| 62-204, F.A.C., Air Pollution Control - General Provisions |  |
| 62-210, F.A.C., Stationary Sources - General Requirements |  |
| 62-212, F.A.C., Stationary Sources - Preconstruction Review |  |
| 62-213, F.A.C., Title V Major Source |  |
| 62-296, F.A.C., Stationary Sources - Emission Standards 62-296.570(4)(a)3. 62-296.570(4)(b)7. | 013, 014, 015, 019, 020 |
| 62-297, F.A.C., Stationary Sources - Emissions Monitoring |  |

Table of Contents

The following conditions apply facility-wide to all emission units and activities:

- Appendices.  The permittee shall comply with all documents identified in Section IV, Appendices, listed in the Table of Contents.  Each document is an enforceable part of this permit unless otherwise indicated.

[Rule 62-213.440, F.A.C.]

Emissions and Controls

- Not federally Enforceable.  Objectionable Odor Prohibited.  No person shall cause, suffer, allow or permit the discharge of air pollutants, which cause or contribute to an objectionable odor. An “objectionable odor” means any odor present in the outdoor atmosphere which by itself or in combination with other odors, is or may be harmful or injurious to human health or welfare, which unreasonably interferes with the comfortable use and enjoyment of life or property, or which creates a nuisance.  [Rule 62-296.320(2) and 62-210.200(Definitions), F.A.C.; and Permit No. 0310028-023-AC]

- General Volatile Organic Compounds (VOC) Emissions or Organic Solvents (OS) Emissions.  The permittee shall allow no person to store, pump, handle, process, load, unload or use in any process or installation, volatile organic compounds or organic solvents without applying known and existing vapor emission control devices or systems deemed necessary and ordered by the Department. [Rule 62-296.320(1), F.A.C.]

{Permitting Note:  Nothing is deemed necessary and ordered at this time.}

- General Visible Emissions.  No person shall cause, let, permit, suffer or allow to be discharged into the atmosphere the emissions of air pollutants from any activity equal to or greater than 20% opacity. This regulation does not impose a specific testing requirement.  [Rule 62-296.320(4)(b), F.A.C.; and Rule 2.1101, JEPB]

- Unconfined Particulate Matter.  No person shall cause, let, permit, suffer or allow the emissions of unconfined particulate matter from any activity, including vehicular movement; transportation of materials; construction; alteration; demolition or wrecking; or industrially related activities such as loading, unloading, storing or handling; without taking reasonable precautions to prevent such emissions. Reasonable precautions to prevent emissions of unconfined particulate matter at this facility include:

- Paving and maintenance of roads, parking areas and yards

- Application of water or chemicals to control emissions from such activities as demolition of buildings, grading roads, construction, and land clearing

- Application of asphalt, water, oil, chemicals, or other dust suppressants to unpaved roads, yards, open stock piles, and similar sources.

- Removal of particulate matter from buildings or work area to prevent particulate from becoming airborne.

- Landscaping or planting of vegetation.

- Use of hoods, fans, filters, and similar equipment to contain, capture and/or vent particulate matter.

- Confining abrasive blasting where possible.

- Enclosure or covering of conveyor systems.

[Rule 62-296.320(4)(c), F.A.C.; and, proposed by applicant in Title V air operation permit renewal application received August 9, 2019.]

Reports and Fees

See Appendix RR, Facility-wide Reporting Requirements for additional details.

- Electronic Annual Operating Report and Title V Annual Emissions Fees. The information required by the Annual Operating Report for Air Pollutant Emitting Facility [Including Title V Source Emissions Fee Calculation] (DEP Form No. 62-210.900(5)) shall be submitted by April 1 of each year, for the previous calendar year, to the Department of Environmental Protection’s (DEP) Division of Air Resource Management.  Each Title V source shall submit the annual operating report using the DEP’s Electronic Annual Operating Report (EAOR) software, unless the Title V source claims a technical or financial hardship by submitting DEP Form No. 62-210.900(5) to the DEP Division of Air Resource Management instead of using the reporting software.  Emissions shall be computed in accordance with the provisions of subsection 62-210.370(2), F.A.C. Each Title V source must pay between January 15 and April 1 of each year an annual emissions fee in an amount determined as set forth in subsection 62-213.205(1), F.A.C. The annual fee shall only apply to those regulated pollutants, except carbon monoxide and greenhouse gases, for which an allowable numeric emission-limiting standard is specified in the source’s most recent construction permit or operation permit. Upon completing the required EAOR entries, the EAOR Title V Fee Invoice can be printed by the source showing which of the reported emissions are subject to the fee and the total Title V Annual Emissions Fee that is due. The submission of the annual Title V emissions fee payment is also due (postmarked) by April 1st of each year. A copy of the system-generated EAOR Title V Annual Emissions Fee Invoice and the indicated total fee shall be submitted to:  Major Air Pollution Source Annual Emissions Fee, Post Office Box 3070, Tallahassee, Florida 32315-3070.  Additional information is available by accessing the Title V Annual Emissions Fee On-line Information Center at the following Internet web site:  http://www.dep.state.fl.us/air/emission/tvfee.htm.  [Rules 62-210.370(3), 62-210.900 & 62-213.205, F.A.C.; and, §403.0872(11), Florida Statutes (2013)]

{Permitting Note:  Resources to help you complete your AOR are available on the electronic AOR (EAOR) website at:  http://www.dep.state.fl.us/air/emission/eaor. If you have questions or need assistance after reviewing the information posted on the EAOR website, please contact the Department by phone at (850) 717-9000 or email at eaor@dep.state.fl.us.}

{Permitting Note:  The Title V Annual Emissions Fee form (DEP Form No. 62-213.900(1)) has been repealed.  A separate Annual Emissions Fee form is no longer required to be submitted by March 1st each year.}

- Annual Statement of Compliance. The permittee shall submit an annual statement of compliance to the compliance authority at the address shown on the cover of this permit and to the US. EPA at the address shown below within 60 days after the end of each calendar year during which the Title V air operation permit was effective.  [Rules 62-213.440(3)(a)2. & 3. and (b), F.A.C.]

U.S. Environmental Protection Agency, Region 4

Atlanta Federal Center

61 Forsyth Street, SW

Atlanta, Georgia 30303

Attn:  Air Enforcement Branch

- Prevention of Accidental Releases (Section 112(r) of CAA).

  - As required by Section 112(r)(7)(B)(iii) of the CAA and 40 CFR 68, the Permittee shall submit an updated Risk Management Plan (RMP) to the Chemical Emergency Preparedness and Prevention Office (CEPPO) RMP Reporting Center.  (See paragraph e., below.)

  - As required under Section 252.941(1)(c), F.S., the Permittee shall report to the appropriate representative of the Division of Emergency Management, as established by department rule, within one working day of discovery of an accidental release of a regulated substance from the stationary source, if the Permittee is required to report the release to the United States Environmental Protection Agency under Section 112(r)(6) of the CAA.

  - The Permittee shall submit the required annual registration fee to the Division of Emergency Management on or before April 1, in accordance with Part IV, Chapter 252, F.S., and Rule 27P-21, F.A.C.

  - Any required written reports, notifications, certifications, and data required to be sent to the Division of Emergency Management, should be sent to:  Division of Emergency Management, 2555 Shumard Oak Boulevard, Tallahassee, FL  32399-2100, Telephone:  (850) 413-9970, Fax:  (850) 488-1739.

  - Any Risk Management Plans, original submittals, revisions, or updates to submittals, should be sent electronically through EPA’s Central Data Exchange system at the following address: https://cdx.epa.gov.  Information on electronically submitting risk management plans using the Central Data Exchange system is available at: http://www2.epa.gov/rmp. The RMP Reporting Center can be contacted at:  RMP Reporting Center, Post Office Box 10162, Fairfax, VA  22038, Telephone:  (703) 227-7650.

  - Any required reports to be sent to the National Response Center, should be sent to:  National Response Center, EPA Office of Solid Waste and Emergency Response, 1200 Pennsylvania Avenue Northwest, Mail Code:  USEPA (5101T), Washington, DC  20460, Telephone:  (800) 424-8802.

  - Send the required annual registration fee using approved forms made payable to:  Cashier, Division of Emergency Management, State Emergency Response Commission, 2555 Shumard Oak Boulevard, Tallahassee, FL  32399-2149

[Part IV, Chapter 252, F.S.; and, Rule 27P-21, F.A.C.]

- Semi-Annual Monitoring Reports. The permittee shall monitor compliance with the terms and conditions of this permit and shall submit reports of any deviations from the requirements of these conditions at least every six (6) months.  All instances of deviations from permit requirements must be clearly identified in such reports, including reference to the specific requirement and the duration of such deviation. All reports shall be accompanied by a certification by a responsible official, pursuant to subsection 62-213.420(4), F.A.C.  (See also Conditions RR2. – RR4. of Appendix RR, Facility-wide Reporting Requirements, for additional reporting requirements related to deviations.)

[Rule 62-213.440(1)(b)3.a., F.A.C.; Rule 2.501, JEPB]

{Permitting Note:  EPA has clarified that, pursuant to 40 CFR 70.6(a)(3), the word “monitoring” is used in a broad sense and means monitoring (i.e., paying attention to) the compliance of the source with all emissions limitations, standards, and work practices specified in the permit.}

Table of Contents

The specific conditions in this section apply to the following emissions unit:

| EU No. | Brief Description |
| --- | --- |
| 013 | 2.5 MW Diesel Electric Generator EMD #1. The engine is operated with Diesel Oxidation Catalyst pollution control. |
| 014 | 2.5 MW Diesel Electric Generator EMD #2. The engine is operated with Diesel Oxidation Catalyst pollution control. |
| 015 | 2.5 MW Diesel Electric Generator EMD #3. The engine is operated with Diesel Oxidation Catalyst pollution control. |
| 019 | 2.865 MW Diesel Electric Generator EMD #4. The engine is operated with Diesel Oxidation Catalyst pollution control. |
| 020 | 2.865 MW Diesel Electric Generator EMD #5. The engine is operated with Diesel Oxidation Catalyst pollution control. |

{Permitting Notes: Each engine in each emissions unit is regulated under 40 CFR 63, Subpart ZZZZ - National Emissions Standards for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines and 40 CFR 63, Subpart A- General Provisions and Rule 62-296.570(4)(b)7, F.A.C.}

The following table provides important details for this emissions unit:

| EU ID No. | Generator Rating MW | Fuel | ICE Class | Mfg | Model Number | Date of Construction | Engine Brake HP | Displacement liters/cylinder(l/c) | Class |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 013 | 2.5 | ULSD | Non-Emergency RICE | Electro-Motive Division | EMD 20-645E4B |  | 3600 |  | Existing RICE >500 bhp |
| 014 | 2.5 | ULSD | Non-Emergency RICE | Electro-Motive Division | EMD 20-645E4B |  | 3600 |  | Existing RICE >500 bhp |
| 015 | 2.5 | ULSD | Non-Emergency RICE | Electro-Motive Division | EMD 20-645E4B |  | 3600 |  | Existing RICE >500 bhp |
| 019 | 2.865 | ULSD | Non-Emergency RICE | Electro-Motive Division | 20-645F4B |  | 4000 |  | Existing RICE >500 bhp |
| 020 | 2.865 | ULSD | Non-Emergency RICE | Electro-Motive Division | 20-645F4B |  | 4000 |  | Existing RICE >500 bhp |

This permit section addresses “existing” stationary CI Non-Emergency RICE greater than 500 HP that are located at an area source of HAP and that have not been modified or reconstructed after 6/12/2006.  Unless the CI RICE are modified or reconstructed after 7/11/2005, NSPS 40 CFR 60, Subpart IIII will not apply.

{Permitting note:  The facility has an agreement with the local utility, that the facility provide peak shaving or non-emergency demand response, in exchange for financial incentives to the facility.  Due to this agreement, the generators are not considered emergency generators under Federal Rule 40 CFR 63 Subpart ZZZZ.}

{Permitting Note: During the next Title V renewal or air construction permit modification, whichever comes first, the facility-wide potential individual (i.e., formaldehyde, etc.) and total HAP emissions need to be provided by the facility in the submitted permit application.}

Performance Restrictions

- Authorized Fuel.  Each engine shall use diesel fuel that meets the following requirements of 40 CFR 80.510(b) for nonroad diesel fuel:

      - Sulfur content:  15ppm maximum for NR diesel fuel

      - Cetane index or aromatic content, as follows:

- A minimum cetane index of 40; or

- A maximum aromatic content of 35 volume percent.

[40 CFR 63.6604(a); 40 CFR 80.510(b)(1)(i), (b)(2); Rule 62-204.800(11)(b)82., F.A.C.; and Permit No. 0250476-004-AC.]

- Fuel Consumption.  The maximum consumption of No. 2 fuel oil allowed to be burned in Units No. 013, 014, 015, 019, and 020 combined shall not exceed 725,000 gallons in any consecutive 12-month period.

{Permitting note: At 100% engine load, each model 20-645E4B engine has a fuel consumption of approximately 196.4 gallons per hour, and each model 20-645F4B engine has a fuel consumption of approximately 197.1 gallons per hour, based on a heat input of 27.1 MMBtu/hr and 27.2 MMBtu/hr, respectively, and a 36-degree API diesel fuel higher heating value of 19,640 Btu/lb. and density of 7.034 lb. /gal.}

[Rule 62-210.200(PTE), F.A.C., Permit No. 0250476-004-AC]

- Hours of Operation.  Each engine in this emissions unit may operate continuously (8,760 hours/year).

[Rule 62-210.200(PTE), F.A.C.; and Permit No. 0250476-004-AC]

- Engine Operation during Startup.  The Permittee shall minimize the engine's time spent at idle during startup and minimize the engine's startup time to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes, after which time the emission standards applicable to all times other than startup in Specific Condition A.7. apply.

[40 CFR 63.6625(h); and Rule 62-204.800(11)(b)82., F.A.C.]

- Engine Operation during startup/shutdown/malfunction.  In order to minimize excess emissions during startup/shutdown/malfunction, these emissions units shall adhere to best operational practices.

[Rule 62-210.700, F.A.C.; and Permit No. 0250476-004-AC]

Excess Emissions. Rule 62-210.700 (Excess Emissions), F.A.C. cannot vary any requirement of an NSPS, NESHAP or Acid Rain program provision.

Emission Limitations and Standards

Unless otherwise specified, the averaging time for Specific Conditions A.7., A.8, and A.9. are based on the specified averaging time of the applicable test method.

- Operating Limitations.  Except during periods of startup, the permittee shall meet the following operating limitations for each engine:

  - Maintain the catalyst so that the pressure drop across the catalyst does not change by more than 2 inches of water from the pressure drop across the catalyst that was measured during the initial performance test; and

  - Maintain the temperature of the engine’s exhaust so that the catalyst inlet temperature is greater than or equal to 450 degrees Fahrenheit and less than or equal to 1350 degrees Fahrenheit.

{Permitting Note: Sources may petition the EPA pursuant to the requirements of 40 CFR 63.8(f) for a different temperature range.}

[40 CFR 63.6603(a), Table 2b, Item 2; Rule 62-204.800(11)(b)82., F.A.C.]

- CO Emissions.  The permittee shall meet the following carbon monoxide (CO) emission standards for each engine of each emissions unit:

  - Limit the concentration of carbon monoxide (CO) in the exhaust to 23 ppmvd at 15% O2; or

  - Reduce CO emissions by 70 percent or more.

[40 CFR 63.6603(a), Table 2d, Item 3; Rule 62-204.800(11)(b)82., F.A.C.]

- NOx Emissions.  The Permittee shall not exceed the following NOx emission standards for each engine of each emissions unit:

  - Emissions Units 013, 014, and 015 (Model 20-645E4B engine): 2.15 lb/MMBtu.

  - Emissions Units 019 and 020 (Model 20-645F4B engine): 2.75 lb/MMBtu.

  - Emissions Units 013, 014, 015, 019, and 020: 4.75 lbs/MMBtu.  This emissions limit shall apply at all times except during periods of startup, shutdown, or malfunction as provided by Rule 62-210.700, F.A.C. (RACT Rule).

  - 137.6 tons per year combined emissions from Emissions Units 013, 014, 015, 019, and 020.

[Rule 62-210.200(PTE), F.A.C.; Rule 62-296.570(2), F.A.C. (RACT); Rule 62-296.570(4)(b)7., F.A.C. (RACT); Rule 62-296.570(4)(c), F.A.C. (RACT); and Permit No. 0250476-004-AC]

- Visible emissions.  Visible Emissions for each engine of each emissions unit shall be less than 20% opacity.

[Rule 62-296.320, F.A.C.; and Permit No. 0250476-004-AC]

General Compliance Requirements

- Continuous Compliance.  The Permittee shall be in compliance with the emission limitations, operating limitations, and other requirements in in 40 CFR 63 Subpart ZZZZ that applies at all times.

[40 CFR 63.6605(a); and Rule 62-204.800(11)(b)82., F.A.C.]

- Operation and Maintenance of Equipment.  At all times the Permittee shall operate and maintain any affected source, including associated air pollution control equipment and monitoring equipment, in a manner consistent with safety and good air pollution control practices for minimizing emissions.  The general duty to minimize emissions does not require the Permittee to make any further efforts to reduce emissions if levels required by this standard have been achieved.  Determination of whether such operation and maintenance procedures are being used will be based on information available to the Department which may include, but is not limited to, monitoring results, review of operation and maintenance procedures, review of operation and maintenance records, and inspection of the source.

[40 CFR 63.6605(b); 40 CFR 63.6670; and Rule 62-204.800(11)(b)82., F.A.C.]

Monitoring of Operations

- Continuous Parameter Monitoring System- Each Engine.  The permittee is required to install a continuous parameter monitoring system (CPMS) as specified in Table 5 of 40 CFR 63 Subpart ZZZZ to continuously monitor catalyst inlet temperature, and shall install, operate, and maintain each CPMS according to the requirements in paragraphs a. through f. of this Specific Condition.

- The Permittee shall prepare a site-specific monitoring plan that addresses the monitoring system design, data collection, and the quality assurance and quality control elements outlined in paragraphs a.(1). through (4) of this Specific Condition and in 40 CFR 63.8(d). As specified in 40 CFR 63.8(f)(4), the Permittee may request approval of monitoring system quality assurance and quality control procedures alternative to those specified in paragraphs a. through f.of this Specific Condition in the site-specific monitoring plan.

    - The performance criteria and design specifications for the monitoring system equipment, including the sample interface, detector signal analyzer, and data acquisition and calculations;

    - Sampling interface (e.g., thermocouple) location such that the monitoring system will provide representative measurements;

    - Equipment performance evaluations, system accuracy audits, or other audit procedures;

    - Ongoing operation and maintenance procedures in accordance with provisions in 40 CFR 63.8(c)(1) and (c)(3); and

    - Ongoing reporting and recordkeeping procedures in accordance with provisions in 40 CFR 63.10(c), (e)(1), and (e)(2)(i).

- The Permittee shall install, operate, and maintain each CPMS in continuous operation according to the procedures in the site-specific monitoring plan.

- The CPMS shall collect data at least once every 15 minutes (see also Specific Condition A.14.).

- For a CPMS for measuring temperature range, the temperature sensor shall have a minimum tolerance of 2.8 degrees Celsius (5 degrees Fahrenheit) or 1 percent of the measurement range, whichever is larger.

- The Permittee shall conduct the CPMS equipment performance evaluation, system accuracy audits, or other audit procedures specified in the site-specific monitoring plan at least annually.

- The permittee shall conduct a performance evaluation of each CPMS in accordance with the site-specific monitoring plan.

[40 CFR 63.6625(b), Table 5 to 40 CFR 63 Subpart ZZZZ, Item 1; and Rule 62-204.800(11)(b)82., F.A.C.]

- Closed Crankcase Ventilation System.  If the engine is not equipped with a closed crankcase ventilation system, the Permittee shall comply with either paragraph a. or paragraph b.  The Permittee shall follow the manufacturer's specified maintenance requirements for operating and maintaining the open or closed crankcase ventilation systems and replacing the crankcase filters, or can request the Department to approve different maintenance requirements that are as protective as manufacturer requirements.

- Install a closed crankcase ventilation system that prevents crankcase emissions from being emitted to the atmosphere, or

- Install an open crankcase filtration emission control system that reduces emissions from the crankcase by filtering the exhaust stream to remove oil mist, particulates and metals.

[40 CFCR 63.6625(g), Rule 62-204.800(11)(b)82., F.A.C.]

- Continuous Compliance Requirements

The Permittee shall monitor and collect data as follows:

  - Except for monitor malfunctions, associated repairs, required performance evaluations, and required quality assurance or control activities, the Permittee shall monitor continuously at all times that the stationary RICE is operating. A monitoring malfunction is any sudden, infrequent, not reasonably preventable failure of the monitoring to provide valid data. Monitoring failures that are caused in part by poor maintenance or careless operation are not malfunctions.

  - The Permittee may not use data recorded during monitoring malfunctions, associated repairs, and required quality assurance or control activities in data averages and calculations used to report emission or operating levels. The Permittee shall, however, use all the valid data collected during all other periods.

[40 CFR 63.6635(a),(b),(c); and Rule 62-204.800(11)(b)82., F.A.C.]

- Continuous Compliance Demonstration Requirements.  The Permittee shall demonstrate continuous compliance with each emission limitation, operating limitation and other requirements in Specific Conditions A.6. and A.7. according to the below methods:

- Conduct performance tests every 8,760 hours or 3 years, whichever comes first, for CO to demonstrate that the required CO percent reduction is achieved or that the emissions remain at or below the CO concentration limit stated in Specific Condition A.7.; and

- Collect the catalyst inlet temperature data according to Specific Condition A.12.; and

- Reduce these data to 4-hour rolling averages; and

- Maintain the 4-hour rolling averages within the operating limitations for the catalyst inlet temperature; and

- Measure the pressure drop across the catalyst once per month and demonstrating that the pressure drop across the catalyst is within the operating limitation established during the performance test.

[40 CFR 63.6640(a), Table 6 of 40 CFR 63 Subpart ZZZZ Item 10; and Rule 62-204.800(11)(b)82., F.A.C.]

Test Methods and Procedures

- NOx Annual Compliance Tests Required.  During each calendar year (January 1st to December 31st), each EU shall be tested to demonstrate compliance with the emissions standards for NOx in Specific Condition A.8.  The test method shall be EPA Method 7 or 7E, as described in 40 CFR 60, Appendix A, adopted by reference in Rule 62-204.800, F.A.C.

RACT Rule: Annual compliance testing while firing diesel fuel oil is unnecessary for units operating on diesel fuel oil for less than 400 hours in the current federal fiscal year.

[Rule 62-297.310(8), F.A.C.; Rule 62-296.570(4)(a)3, F.A.C. (RACT); and Permit No. 0250476-004-AC]

- Visible Emissions Compliance Tests Required.  During each calendar year (January 1st to December 31st), each EU shall be tested to demonstrate compliance with the emissions standards for Visible Emissions in Specific Condition A.9.  The test method shall be EPA Method 9 as described in 40 CFR 60, Appendix A and adopted by reference in Rule 62-204.800, F.A.C.

[Rules 62-204.800, 62-297.310(8), F.A.C.; and Permit No. 0250476-004-AC]

- CO - Performance Testing- Required.  The Permittee shall conduct performance tests every 8,760 hours or 3 years, whichever comes first, in accordance with 40 CFR 63 Subpart ZZZZ requirements to demonstrate compliance with the emissions standards for CO in Specific Condition A.7.

[40 CFR63.6615, Table 3 to 40 CFR 63 Subpart ZZZZ, Item 4; and Rule 62-204.800(11)(b)82., F.A.C.]

- Fuel Oil Fuel Analysis.  The fuel oil shall be monitored for the sulfur content using ASTM D4294 Method (or equivalent), or by maintaining records of fuel oil sulfur content certifications, as provided by the fuel supplier. For each load of fuel oil delivered to the facility, the permittee shall either:

- Obtain a copy of the fuel analysis from the supplier.  Methods for determining the fuel sulfur content of the distillate oil shall be ASTM Method D 129-91, D 1552-95, D 2622-94, D 4294-98 or comparable Department approved method.  Records shall specify the test method used.  Or

- Collect a fuel sample to be sent for laboratory analysis based on one of the following method: ASTM Method D 129-91, D 1552-95, D 2622-94, D 4294-98 or comparable Department approved method. Or

- Records from the fuel supplier that indicates the fuel delivered is Low Sulfur No. 2 Diesel fuel oil by ASTM Method 975-98b, or current version.  Specification for Diesel Fuel Oils provides for this classification of diesel fuel oils as having no more than 0.05 percent sulfur content by weight.

[Rule 62-297.440, F.A.C.; and Permit No. 0250476-004-AC]

- Test Methods.  When required, tests shall be performed in accordance with Table 4 to 40 CFR 63 Subpart ZZZZ as follows:

| For each | Complying with the requirement to . . . | You must . . . | Using . . . | According to the following requirements . . . |
| --- | --- | --- | --- | --- |
| 1. 2SLB, 4SLB, and CI stationary RICE | a. reduce CO emissions | i. Select the sampling port location and the number/location of traverse points at the inlet and outlet of the control device; and |  | (a) For CO and O2 measurement, ducts ≤6 inches in diameter may be sampled at a single point located at the duct centroid and ducts >6 and ≤12 inches in diameter may be sampled at 3 traverse points located at 16.7, 50.0, and 83.3% of the measurement line (`3-point long line'). If the duct is >12 inches in diameter and the sampling port location meets the two and half-diameter criterion of Section 11.1.1 of Method 1 of 40 CFR part 60, appendix A-1, the duct may be sampled at `3-point long line'; otherwise, conduct the stratification testing and select sampling points according to Section 8.1.2 of Method 7E of 40 CFR part 60, appendix A-4. |
|  |  | ii. Measure the O2 at the inlet and outlet of the control device; and | (1) Method 3 or 3A or 3B of 40 CFR part 60, appendix A-2, or ASTM Method D6522-00 (Reapproved 2005)a c (heated probe not necessary) | (b) Measurements to determine O2 must be made at the same time as the measurements for CO concentration |
|  |  | iii. Measure the CO at the inlet and the outlet of the control device | (1) ASTM D6522-00 (Reapproved 2005)a b c (heated probe not necessary) or Method 10 of 40 CFR part 60, appendix A-4 | (c) The CO concentration must be at 15 percent O2, dry basis. |
| 3. Stationary RICE | a. limit the concentration of CO in the stationary RICE exhaust | i. Select the sampling port location and the number/location of traverse points at the exhaust of the stationary RICE; and |  | (a) For CO, O2, and moisture measurement, ducts ≤6 inches in diameter may be sampled at a single point located at the duct centroid and ducts >6 and ≤12 inches in diameter may be sampled at 3 traverse points located at 16.7, 50.0, and 83.3% of the measurement line (`3-point long line'). If the duct is >12 inches in diameter and the sampling port location meets the two and half-diameter criterion of Section 11.1.1 of Method 1 of 40 CFR part 60, appendix A, the duct may be sampled at `3-point long line'; otherwise, conduct the stratification testing and select sampling points according to Section 8.1.2 of Method 7E of 40 CFR part 60, appendix A. If using a control device, the sampling site must be located at the outlet of the control device. |
|  | ii. Determine the O2 concentration of the stationary RICE exhaust at the sampling port location; and | (1) Method 3 or 3A or 3B of 40 CFR part 60, appendix A-2, or ASTM Method D6522-00 (Reapproved 2005)a (heated probe not necessary) | (a) Measurements to determine O2 concentration must be made at the same time and location as the measurements for CO concentration. | ii. Determine the O2 concentration of the stationary RICE exhaust at the sampling port location; and |
|  | iii. Measure moisture content of the stationary RICE exhaust at the sampling port location; and | (1) Method 4 of 40 CFR part 60, appendix A-3, or Method 320 of 40 CFR part 63, appendix A, or ASTM D 6348-03a | (a) Measurements to determine moisture content must be made at the same time and location as the measurements for CO concentration. | iii. Measure moisture content of the stationary RICE exhaust at the sampling port location; and |
|  | iv. measure CO at the exhaust of the stationary RICE | (1) Method 10 of 40 CFR part 60, appendix A-4, ASTM Method D6522-00 (2005)a c, Method 320 of 40 CFR part 63, appendix A, or ASTM D6348-03a | (a) CO concentration must be at 15 percent O2, dry basis. Results of this test consist of the average of the three 1-hour or longer runs. | v. measure CO at the exhaust of the stationary RICE |

a	The Permittee may also use Methods 3A and 10 as options to ASTM-D6522-00 (2005). The permittee may obtain a copy of ASTM-D6522-00 (2005) from at least one of the following addresses: American Society for Testing and Materials, 100 Barr Harbor Drive, West Conshohocken, PA 19428-2959, or University Microfilms International, 300 North Zeeb Road, Ann Arbor, MI 48106.

b	The Permittee may obtain a copy of ASTM-D6348-03 from at least one of the following addresses: American Society for Testing and Materials, 100 Barr Harbor Drive, West Conshohocken, PA 19428-2959, or University Microfilms International, 300 North Zeeb Road, Ann Arbor, MI 48106.

The above methods are described in 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.

[40 CFR 63.6620(a), Table 4 to 40 CFR 63 Subpart ZZZZ Item 1 for 2SLB, 4SLB and CI stationary RICE, Item 3 for Stationary RICE, Rule 62-204.800(11)(b)82., F.A.C.]

- Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.

[Rule 62-297.310, F.A.C.]

{Permitting Note: Air compliance test notifications can now be completed online in the Department’s Business Portal. To access this online process, go to http://www.fldepportal.com/go/home and sign in (or register if you’re a new user) from the link in the upper right corner of the page. On the Welcome page select the Submit option, then select Registration/Notification, and then click on Air Compliance Test Notifications.  Once in the process, just carefully read the instructions on each screen (and under the Help tabs) to complete the notification.}

- Performance Testing- Non-Operational Engine.  If the permittee owns or operates a non-operational stationary RICE that is subject to performance testing, the permittee does not need to start up the engine solely to conduct the performance test.  The permittee can conduct the performance test when the engine is started up again.

[40 CFR 63.6620(b), Rule 62-204.800(11)(b)82., F.A.C.]

- Performance Testing- Test Runs.  Each performance test shall consist of three separate test runs, as specified in 40 CFR 63.7(e)(3).  Each test run shall last at least 1 hour.

[40 CFR 63.6620(d); and Rule 62-204.800(11)(b)82., F.A.C.]

- Performance Testing.

- The Permittee shall use Equation 1 to determine compliance with the percent reduction requirement:

Where:

Ci = concentration of carbon monoxide (CO) at the control device inlet,

Co = concentration of CO at the control device outlet, and

R = percent reduction of CO.

- The Permittee shall normalize the CO concentrations at the inlet and outlet of the control device to a dry basis and to 15 percent oxygen, or an equivalent percent carbon dioxide (CO2). If pollutant concentrations are to be corrected to 15 percent oxygen and CO2 concentration is measured in lieu of oxygen concentration measurement, a CO2 correction factor is needed. Calculate the CO2 correction factor as described in paragraphs b.(1). through (3).

- Calculate the fuel-specific Fo value for the fuel burned during the test using values obtained from Method 19, Section 5.2, and the following equation:

Where:

Fo = Fuel factor based on the ratio of oxygen volume to the ultimate CO2 volume produced by the fuel at zero percent excess air.

0.209 = Fraction of air that is oxygen, percent/100.

Fd = Ratio of the volume of dry effluent gas to the gross calorific value of the fuel from Method 19, dsm3/J (dscf/106 Btu).

Fc = Ratio of the volume of CO2 produced to the gross calorific value of the fuel from Method 19, dsm3/J (dscf/106 Btu)

- Calculate the CO2 correction factor for correcting measurement data to 15 percent O2, as follows:

Where:

XCO2 = CO2 correction factor, percent.

5.9 = 20.9 percent O2—15 percent O2, the defined O2 correction value, percent.

- Calculate the CO gas concentration adjusted to 15 percent O2 using CO2 as follows:

Where:

Cadj = Calculated concentration of CO adjusted to 15 percent O2.

Cd = Measured concentration of CO uncorrected.

XCO2 = CO2 correction factor, percent.

%CO2 = Measured CO2 concentration measured, dry basis, percent.

[40 CFR 63.6620(e), Rule 62-204.800(11)(b)82., F.A.C.]

- Performance Testing – Engine Percent Load.  The engine percent load during a performance test shall be determined by documenting the calculations, assumptions, and measurement devices used to measure or estimate the percent load in a specific application.  A written report of the average percent load determination shall be included in the notification of compliance status.

The following information shall be included in the written report: the engine model number, the engine manufacturer, the year of purchase, the manufacturer's site-rated brake horsepower, the ambient temperature, pressure, and humidity during the performance test, and all assumptions that were made to estimate or calculate percent load during the performance test shall be clearly explained.  f measurement devices such as flow meters, kilowatt meters, beta analyzers, stain gauges, etc. are used, the model number of the measurement device, and an estimate of its accurate in percentage of true value shall be provided.

[40 CFR 63.6620(i); Rule 62-204.800(11)(b)82., F.A.C.; and Rule 62-297.310(3), F.A.C]

- Catalyst Change- Reestablishment of Operating Parameter Values and Performance Testing Requirements.  If the catalyst is changed, the values of the operating parameters measured during the initial performance test shall be reestablished.  When reestablishing the values of the operating parameters, a performance test shall be conducted to demonstrate that the emissions units are meeting the required applicable emission limitation.

[40 CFR 63.6640(b); and Rule 62-204.800(11)(b)82., F.A.C.]

Notification Requirements

- The Permittee shall submit all of the notifications in 40 CFR 63.7(b) and (c), 40 CFR 63.8(e), (f)(4) and (f)(6), 40 CFR 63.9(b) through (e), and (g) and (h) that apply by the dates specified.

[40 CFR 63.6645(a)(2); and Rule 62-204.800(11)(b)82., F.A.C.]

- Notification of CO Performance Tests.  The permittee shall notify the Department in writing of the intent to conduct a performance test at least 60 calendar days before the performance test is initially scheduled to begin to allow the Department, upon request, to review and approve the site-specific test plan and have an observer present during the test.

[40 CFR 63.7(b)(1), 40 CFR 63.6645(g), Rule 62-204.800(11)(b)82., F.A.C.]

- Notification of NOx and VE Performance Tests.  The permittee shall notify the Compliance Authority in writing at least 15 days prior to any required tests.  Tests shall be conducted in accordance with the applicable requirements specified in Appendix TR (Facility-wide Testing Requirements) of this permit.

[Rule 62-297.310(9) F.A.C.]

Recordkeeping and Reporting Requirements

- Deviation Reports.  The Permittee shall report each instance in which the emission limitation or operating limitation in Specific Conditions A.6. and A.7. is not met.  These instances are deviations from the emission and operating limitations in 40 CFR 63 Subpart ZZZZ. These deviations shall be reported according to the requirements in Specific Conditions A.37.-A.43.

[40 CFR 63.6640(b); and Rule 62-204.800(11)(b)82., F.A.C.]

- The Permittee shall report each instance in which the requirements in Table 8 of 40 CFR 63 Subpart ZZZZ are not met. Refer to Appendix.

[40 CFR 63.6640(e), Rule 62-204.800(11)(b)82., F.A.C.]

- The Permittee shall keep the records described in this Specific Condition:

  - A copy of each notification and report that is submitted, including all documentation supporting any Initial Notification or Notification of Compliance Status that is submitted according to the requirement in 40 CFR 63.10(b)(2)(xiv).

  - Records of the occurrence and duration of each malfunction of operation (i.e., process equipment) or the air pollution control and monitoring equipment.

  - Records of performance tests and performance evaluations as required in 40 CFR 63.10(b)(2)(viii).

  - Records of all required maintenance performed on the air pollution control and monitoring equipment.

  - Records of actions taken during periods of malfunction to minimize emissions in accordance with Specific Condition A.11., including corrective actions to restore malfunctioning process and air pollution control and monitoring equipment to its normal or usual manner of operation.

[40 CFR 63.6655(a), Rule 62-204.800(11)(b)82., F.A.C.]

- For each CPMS, the Permittee shall keep the following records:

  - Records described in 40 CFR 63.10(b)(2)(vi) through (xi).

  - Previous (i.e., superseded) versions of the performance evaluation plan as required in 40 CFR 63.8(d)(3).

  - Requests for alternatives to the relative accuracy test for CPMS as required in 40 CFR 63.8(f)(6)(i), if applicable.

[40 CFR 63.6655(b), Rule 62-204.800(11)(b)82., F.A.C.]

- The Permittee shall keep the records required in Table 6 of 40 CFR 63 Subpart ZZZZ (stated in Specific Condition A.15.) to show continuous compliance with each emission or operating limitation stated in Specific Conditions A.6. and A.7.

[40 CFR 63.6655(d); and Rule 62-204.800(11)(b)82., F.A.C.]

- Maintenance Records.  The Permittee shall keep records of the maintenance conducted on the stationary RICE in order to demonstrate that the stationary RICE and after-treatment control device were operated and maintained according to your own maintenance plan.

[40 CFR 63.6655(e)(3); and Rule 62-204.800(11)(b)82., F.A.C.]

- Fuel Oil Consumption Records.  The permittee shall maintain daily records of fuel oil consumption for the emission units.

[Rule 62-210.200, F.A.C.; and Permit No. 0250476-004-AC]

- Record Requirements.  Records shall be retained as follows:

  - The Permittee records shall be in a form suitable and readily available for expeditious review according to 40 CFR 63.10(b)(1).

  - As specified in 40 CFR 63.10(b)(1), the Permittee shall keep each record for 5 years following the date of each occurrence, measurement, maintenance, corrective action, report, or record.

  - The Permittee shall keep each record readily accessible in hard copy or electronic form for at least 5 years after the date of each occurrence, measurement, maintenance, corrective action, report, or record, according to 40 CFR 63.10(b)(1).

[40 CFR 63.6660(a),(b),(c), Rule 62-204.800(11)(b)82., F.A.C.]

- Semi-Annual Compliance Report.  The Permittee shall submit a Compliance Report, as required in Table 7 of 40 CFR part 63, subpart ZZZZ, that contains the following information:

    - If there are no deviations from any emission limitations or operating limitations that apply, a statement that there were no deviations from the emission limitations or operating limitations during the reporting period.  If there were no periods during which the CPMS, was out-of-control, as specified in 40 CFR 63.8(c)(7), a statement that there were not periods during which the CMS was out-of-control during the reporting period.  The report shall be submitted semiannually to the Compliance Authority according to the requirements in Specific Condition A.39.; or

    - If the Permittee had a deviation from any emission limitation or operating limitation during the reporting period, the information in Specific Condition A.41.  If there were periods during which the CPMS, was out-of-control, as specified in 40 CFR 63.8(c)(7), the information in Specific Condition A.42.  The report shall be submitted semiannually to the Compliance Authority according to the requirements in Specific Condition A.39.; or

    - If there is a malfunction during the reporting period, the information in Specific Condition A.40.d. shall be stated.  The report shall be submitted semiannually to the Compliance Authority according to the requirements in Specific Condition A.39.

[40 CFR 63.6650(a), Table 7 of 40 CFR 63 Subpart ZZZZ, Item 1, Rule 62-204.800(11)(b)82., F.A.C.]

- Semi-Annual Compliance Report -Submittal Requirement.  The permittee shall submit the report required as specified below:

    - Each compliance report shall cover the semiannual reporting period from January 1 through June 30 or the semiannual reporting period from July 1 through December

    - Each subsequent compliance report shall be postmarked or delivered no later than July 31 or January 31, whichever date is the first date following the end of the semiannual reporting period.

[40 CFR 63.6650(b)(3),(4); and Rule 62-204.800(11)(b)82., F.A.C.]

- Semi-Annual Compliance Report Requirements.  The compliance report shall contain the information in paragraphs a. through f. as specified below:

- Company name and address.

- Statement by a responsible official, with that official's name, title, and signature, certifying the accuracy of the content of the report.

- Date of report and beginning and ending dates of the reporting period.

- If the Permittee had a malfunction during the reporting period, the compliance report shall include the number, duration, and a brief description for each type of malfunction which occurred during the reporting period and which caused or may have caused any applicable emission limitation to be exceeded. The report shall also include a description of actions taken by the permittee during a malfunction of an affected source to minimize emissions in accordance with Specific Condition A.11., including actions taken to correct a malfunction.

- If there are no deviations from any emission or operating limitations that apply to the Permittee, a statement that there were no deviations from the emission or operating limitations during the reporting period.

- If there were no periods during which the CPMS, was out-of-control, as specified in 40 CFR 63.8(c)(7), a statement that there were no periods during which the CPMS was out-of-control during the reporting period.

[40 CFR 63.6650(c); and Rule 62-204.800(11)(b)82., F.A.C.]

- Semi-Annual Compliance Report -Deviation Requirements CMS.  For each deviation from an emission or operating limitation that occurs for a stationary RICE where a CMS is not in use to comply with the emission or operating limitations in this subpart, the compliance report shall contain the information in Specific Condition A.40.a.-d. and the information in paragraphs a. and b. of this Specific Condition.

- The total operating time of the stationary RICE at which the deviation occurred during the reporting period.

- Information on the number, duration, and cause of deviations (including unknown cause, if applicable), as applicable, and the corrective action taken.

[40 CFR 63.6650(d); and Rule 62-204.800(11)(b)82., F.A.C.]

- Semi-Annual Compliance Report -Deviation Requirements CPMS.  For each deviation from an emission or operating limitation occurring for a stationary RICE where the Permittee is using a CPMS to comply with the emission and operating limitations in 40 CFR 63 Subpart ZZZZ, the Permittee shall include information in paragraphs a. through d. of Specific Condition A.40. and paragraphs a.  through l. below.

- The date and time that each malfunction started and stopped.

- The date, time, and duration that each CMS was inoperative, except for zero (low- level) and high-level checks.

- The date, time, and duration that each CMS was out-of-control, including the information in 40 CFR 63.8(c)(8).

- The date and time that each deviation started and stopped, and whether each deviation occurred during a period of malfunction or during another period.

- A summary of the total duration of the deviation during the reporting period, and the total duration as a percent of the total source operating time during that reporting period.

- A breakdown of the total duration of the deviations during the reporting period into those that are due to control equipment problems, process problems, other known causes, and other unknown causes.

- A summary of the total duration of CMS downtime during the reporting period, and the total duration of CMS downtime as a percent of the total operating time of the stationary RICE at which the CMS downtime occurred during that reporting period.

- An identification of each parameter and pollutant (CO) that was monitored at the stationary RICE.

- A brief description of the stationary

- A brief description of the CMS.

- The date of the latest CMS certification or audit.

- A description of any changes in CMS, processes, or controls since the last reporting period.

[40 CFR 63.6650(e), Rule 62-204.800(11)(b)82., F.A.C.]

- Semi-Annual Deviation Report Requirements.  The Permittee shall report all deviations as defined in 40 CFR 63 Subpart ZZZZ in the semi-annual monitoring report required by 40 CFR 70.6 (a)(3)(iii)(A).  If an affected source submits a compliance report pursuant to Table 7 of 40 CFR 63 Subpart ZZZZ along with, or as part of, the semi-annual monitoring report required by 40 CFR 70.6(a)(3)(iii)(A), and the compliance report includes all required information concerning deviations from any emission or operating limitation in 40 CFR 63 Subpart ZZZZ, submission of the compliance report shall be deemed to satisfy any obligation to report the same deviations in the semi-annual monitoring report.  However, submission of a compliance report shall not otherwise affect any obligation the affected source may have to report deviations from permit requirements to the Permit Authority.

[40 CFR 63.6650(f); and Rule 62-204.800(11)(b)82., F.A.C.]

- Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.

[Rule 62-213.440(1)(b), F.A.C.]

Table of Contents

The specific conditions in this section apply to the following emissions unit:

| EU No. | Emission Unit Description |
| --- | --- |
| 021 | 1.2 MW Digester Gas Electric Co-generator (#3) |
| 022 | 1.2 MW Digester Gas Electric Co-generator (#4) |
| 024 | 1.2 MW Digester Gas Electric Co-generator (#1) |
| 025 | 1.2 MW Digester Gas Electric Co-generator (#2) |

These emissions units (EU) each consist of a 1760 brake horsepower, sixteen-cylinder, spark ignition internal combustion engine, Cooper-Superior Model 16GTLD, coupled to a 1.2 megawatt (MW) electrical generator.  The engines are classified as new, non-emergency spark ignition (SI) four-stroke lean burn (4SLB) engines. The co-generators are listed individually but regulated collectively.  These units burn scrubbed digester gas (biogas) produced in the anaerobic digesters and also generate the necessary heat for the anaerobic digesters to achieve and meet the requirements for Processes to Significantly Reduce Pathogens (PSRPs) and reduce Vector Attraction in the production of biosolids applied to Agricultural Land, Forests, or Reclamation Sites for beneficial use.  These cogeneration units also serve a valuable waste-to-energy role by using the scrubbed biogas to reduce hydrogen sulfide (H2S) to produce electricity for in plant use.  The units are equipped with lean burn combustion technology to reduce nitrogen oxides (NOx) emissions.  Three units are operated at one time.

The following table provides important details for these emissions units:

| E.U. ID No. | Generator Rating MW | Primary Fuel | ICE Class | Mfg | Model Number | Engine Brake HP | Date of Construction | Model Year | Displacement liters/cylinder (l/c) | Serial # | Date of last mod. or reconst. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 021 | 1.2 | Digester Gas | Non-Emergency | Cooper-Superior | 16GTLD | 1760 | 2013 | 2013 | 13.519 | 355449 | 2013 |
| 022 | 1.2 | Digester Gas | Non-Emergency | Cooper-Superior | 16GTLD | 1760 | 2013 | 2013 | 13.519 | 355439 | 2013 |
| 024 | 1.2 | Digester Gas | Non-Emergency | Cooper-Superior | 16GTLD | 1760 | 2015 | 2014 | 13.519 | 355789 | 2015 |
| 025 | 1.2 | Digester Gas | Non-Emergency | Cooper-Superior | 16GTLD | 1760 | 2015 | 2014 | 13.519 | 355799 | 2015 |

{Permitting Note: Each emissions unit is regulated under: NSPS - 40 CFR 60, Subpart JJJJ, Standards of Performance for Stationary Spark Ignition Internal Combustion Engines, NESHAP – 40 CFR 63, Subpart ZZZZ, National Emissions Standards for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines adopted and incorporated by reference in Rule 62-204.800, F.A.C.  Compliance with the requirements of 40 CFR 63, Subpart ZZZZ is met by meeting the requirements of 40 CFR 60, Subpart JJJJ.  No further requirements of 40 CFR 63, Subpart ZZZZ apply for any of the engines.

{Permitting Note: During the next Title V renewal or air construction permit modification, whichever comes first, the facility-wide potential individual (i.e., formaldehyde, etc.) and total HAP emissions need to be provided by the facility in the submitted permit application.}

Essential Potential to Emit (PTE) Parameters

- Reciprocating Internal Combustion Engines.  The permittee is authorized to operate four, 1.2 megawatt Cooper-Superior Model 16GTLD engine driven co-generator units fueled with digester gas. These emission units are listed individually but regulated collectively.

[Rule 62-210.200(PTE), F.A.C.; and Permit No. 0250476-013-AC]

- Emissions Unit Operating Rate Limitation After Testing.  See the related testing provisions in Appendix TR, Facility-wide Testing Requirements.

[Rule 62-297.310(3), F.A.C.]

- Authorized Fuel.  Each engine of each emissions unit shall be fired with digester gas (biogas), only.

[Rule 62-210.200(PTE), F.A.C.; and Permit No. 0250476-013-AC]

- Hours of Operation.  The combined hours of operation for Unit Nos. 021, 022, 024, and 025 shall not exceed 26,280 hours in any consecutive 12-month period.

[Rules 62-210.200(PTE), F.A.C.; and Permit No. 0250476-013-AC]

NESHAP and NSPS Applicability

- NESHAP, 40 CFR 63 Subpart ZZZZ Applicability.  Each engine is classified as a new stationary Reciprocating Internal Combustion Engines (RICE) located at an area source of HAP. In accordance with 40 CFR 63.6590(c)(1), the units shall meet the requirements of 40 CFR 63 Subpart ZZZZ by complying with the 40 CFR 60 Subpart JJJJ standards. No further 40 CFR 63 Subpart ZZZZ standards shall apply to these engines.

[40 CFR 63.6675(def); 40 CFR 63.6585(a) & (c); 40 CFR 63.6590(a)(2)(iii); 40 CFR 63.6590(c)(1); and Rule 62-204.800(8), F.A.C.]

- NSPS, 40 CFR 60, Subpart JJJJ Applicability.  These engines are classified as non-emergency spark ignition (SI) four-stroke lean burn (4SLB) engines and are subject to the standards of 40 CFR 60 Subpart JJJJ.

[40 CFR 60.4230(a)(4)(i); and Rule 62-204.800(8), F.A.C.]

- 40 CFR 60, Subpart A-General Provision.  Table 3 to 40 CFR 60 Subpart JJJJ shows which parts of the General Provisions in 40 CFR 60.1 through 40 CFR 60.19 are applicable.

[40 CFR 60.4246; and Rule 62-204.800(8), F.A.C]

Emission Limitations and Standards

Unless otherwise specified, the averaging times for Specific Conditions B.8. through B.10. are based on the specified averaging time of the applicable test method.

- Nitrogen Oxides (NOx) Emissions of each Emissions Unit.

- NOx emissions of each emissions unit shall not exceed 2.0 grams per horsepower hour (g/HP-hr) or 150 parts per million by volume dry (ppmvd) @15%O2.  The Permittee may choose to comply with the emission standards in units of either g/HP-hr or ppmvd at 15 percent O2.

[40 CFR 60.4233(e); Table 1 of Subpart JJJJ of Part 60 CFR; and Rule 62-204.800(8), F.A.C]

- NOx emissions of each emissions unit shall not exceed 1.16 g/HP-hr (4.5 lb/hr).

[Permit No. 0250476-013-AC; and Requested by Facility to avoid PSD Review]

- Carbon Monoxide (CO) Emissions of each Emissions Unit.

- CO emissions of each emissions unit shall not exceed 5.0 g/HP-hr or 610 ppmvd @ 15%O2.  The Permittee of stationary non-certified SI engines may choose to comply with the emission standards in units of either g/HP-hr or ppmvd at 15 percent O2.

[40 CFR 60.4233(e); Table 1 of Subpart JJJJ of Part 60 CFR; Rule 62-204.800(8), F.A.C.]

- CO emissions of each emissions unit shall not exceed 3.0 g/HP-hr (10.8 lb/hr).

[Permit No. 0250476-013-AC, Limit Requested by Facility]

- Volatile Organic Compounds (VOC) Emissions of each Emissions Unit.

- VOC emissions of each emissions unit shall not exceed 1.0 g/HP-hr or 80 ppmvd @ 15%O2 at the outlet of the oxidation catalyst system.  The Permittee may choose to comply with the emission standards in units of either g/HP-hr or ppmvd at 15 percent O2.

[40 CFR 60.4233(e); Table 1 of Subpart JJJJ of Part 60 CFR, Rule 62-204.800(8), F.A.C]

- For purposes of 40 CFR 60 Subpart JJJJ, when calculating emissions of volatile organic compounds, emissions of formaldehyde should not be included.

[40 CFR 60 Subpart JJJJ, Table 1 of Subpart JJJJ of Part 60 CFR, Rule 62-204.800(8), F.A.C.]

- Each Emissions Unit.  Each engine shall be operated and maintained such that it achieves the emission standards as required in 40 CFR 60.4233 [Specific Conditions B.8. through B.10.] over the entire life of the engine.

[40 CFR 60.4234; and Rule 62-204.800(8), F.A.C.]

- Each Emissions Unit.  The Permittee shall demonstrate compliance with the purchase of a non-certified engine and demonstrating compliance with the emission standards specified in 40 CFR 60.4233(e) [Specific Conditions B.8. through B.10.] and the requirements specified in Specific Condition B.14., as applicable, according to Specific Condition B.13.

[40 CFR 60.4243(b)(2); and Rule 62-204.800(8), F.A.C.]

- Compliance Demonstration.  The Permittee shall demonstrate compliance according to paragraphs a. and b. of this Specific Condition:

- Maintenance Plan:  The Permittee shall keep a maintenance plan and records of conducted maintenance and shall, to the extent practicable, maintain and operate the engine in a manner consistent with good air pollution control practice for minimizing emissions.

- Performance Tests.  The Permittee shall conduct performance tests for each pollutant specified in Specific Conditions B.8. through B.10., every 8,760 hours or 3 years, whichever comes first.

[40 CFR 60.4243(b)(2)(ii); 40 CFR 60.8(a); and Rule 62-204.800(8), F.A.C.]

Test Methods and Procedures

- Compliance Test Procedures.  The performance tests shall follow the procedures below.

- Each performance test shall be conducted within 10 percent of 100 percent peak (or the highest achievable) load and according to the requirements in 40 CFR 60.8 and under the specific conditions that are specified by Table 2 of 40 CFR 60 Subpart JJJJ.

- Performance tests during periods of startup, shutdown, or malfunction are not allowed, as specified in 40 CFR 60.8(c).  If the stationary SI internal combustion engine is non-operational, it is not necessary to startup the engine solely to conduct a performance test; however, the performance test shall be conducted immediately upon startup of the engine.

- Three separate test runs shall be conducted for each performance test required, as specified in 40 CFR 60.8(f).  Each test run shall be conducted within 10 percent of 100 percent peak (or the highest achievable) load and last at least 1 hour.

- To determine compliance with the NOx mass per unit output emission limitation, the concentration of NOx in the engine exhaust should be converted using Equation 1, below:

Where:

ER = Emission rate of NOX in g/HP-hr.

Cd = Measured NOX concentration in parts per million by volume (ppmv).

1.912×10−3 = Conversion constant for ppm NOX to grams per standard cubic meter at 20 degrees Celsius.

Q = Stack gas volumetric flow rate, in standard cubic meter per hour, dry basis.

T = Time of test run, in hours.

HP-hr = Brake work of the engine, horsepower-hour (HP-hr).

e.	To determine compliance with the CO mass per unit output emission limitation, convert the concentration of CO in the engine exhaust using Equation 2 of this section:

Where:

ER = Emission rate of CO in g/HP-hr.

Cd = Measured CO concentration in ppmv.

1.164×10−3 = Conversion constant for ppm CO to grams per standard cubic meter at 20 degrees Celsius.

Q = Stack gas volumetric flow rate, in standard cubic meters per hour, dry basis.

T = Time of test run, in hours.

HP-hr = Brake work of the engine, in HP-hr.

f.	When calculating emissions of VOC, for the purposes of 40 CFR 60 Subpart JJJJ, emissions of formaldehyde should not be included.  To determine compliance with the VOC mass per unit output emission limitation, convert the concentration of VOC in the engine exhaust using Equation 3 of this section:

Where:

ER = Emission rate of VOC in g/HP-hr.

Cd = VOC concentration measured as propane in ppmv.

1.833×10−3 = Conversion constant for ppm VOC measured as propane, to grams per standard cubic meter at 20 degrees Celsius.

Q = Stack gas volumetric flow rate, in standard cubic meters per hour, dry basis.

T = Time of test run, in hours.

HP-hr = Brake work of the engine, in HP-hr.

g.	If the Permittee chooses to measure VOC emissions using either Method 18 of 40 CFR part 60, appendix A, or Method 320 of 40 CFR part 63, appendix A, then it has the option of correcting the measured VOC emissions to account for the potential differences in measured values between these methods and Method 25A.  The results from Method 18 and Method 320 can be corrected for response factor differences using Equations 4 and 5 of this section.  The corrected VOC concentration can then be placed on a propane basis using Equation 6 of this section.

Where:

RFi = Response factor of compound i when measured with EPA Method 25A.

CM i = Measured concentration of compound i in ppmv as carbon.

CA i = True concentration of compound i in ppmv as carbon.

Where:

Ci corr = Concentration of compound i corrected to the value that would have been measured by EPA Method 25A, ppmv as carbon.

Ci meas = Concentration of compound i measured by EPA Method 320, ppmv as carbon.

Where:

CPeq = Concentration of compound i in mg of propane equivalent per DSCM.

[40 CFR 60.4244; and Rule 62-204.800(8), F.A.C.]

- Table 2 to Subpart JJJJ of Part 60—Requirements for Performance Tests.

| For each | Complying with the requirement to | You must | Using | According to the following requirements |
| --- | --- | --- | --- | --- |
| 1. Stationary SI internal combustion engine demonstrating compliance according to §60.4244. | a. limit the concentration of NOX in the stationary SI internal combustion engine exhaust. | i. Select the sampling port location and the number/location of traverse points at the exhaust of the stationary internal combustion engine; | (1) Method 1 or 1A of 40 CFR part 60, appendix A-1, if measuring flow rate | (a) Alternatively, for NOX, O2, and moisture measurement, ducts ≤6 inches in diameter may be sampled at a single point located at the duct centroid and ducts >6 and ≤12 inches in diameter may be sampled at 3 traverse points located at 16.7, 50.0, and 83.3% of the measurement line ('3-point long line'). If the duct is >12 inches in diameter and the sampling port location meets the two and half-diameter criterion of Section 11.1.1 of Method 1 of 40 CFR part 60, Appendix A, the duct may be sampled at '3-point long line'; otherwise, conduct the stratification testing and select sampling points according to Section 8.1.2 of Method 7E of 40 CFR part 60, Appendix A. |
|  |  | ii. Determine the O2 concentration of the stationary internal combustion engine exhaust at the sampling port location; | (2) Method 3, 3A, or 3Bb of 40 CFR part 60, appendix A-2 or ASTM Method D6522-00 (Reapproved 2005)ae | (b) Measurements to determine O2 concentration must be made at the same time as the measurements for NOX concentration. |
|  |  | iii. If necessary, determine the exhaust flowrate of the stationary internal combustion engine exhaust; | (3) Method 2 or 2C of 40 CFR part 60, appendix A-1 or Method 19 of 40 CFR part 60, appendix A-7 |  |
|  |  | iv. If necessary, measure moisture content of the stationary internal combustion engine exhaust at the sampling port location; and | (4) Method 4 of 40 CFR part 60, appendix A-3, Method 320 of 40 CFR part 63, appendix A, or ASTM Method D 6348-03e | (c) Measurements to determine moisture must be made at the same time as the measurement for NOX concentration. |
|  |  | v. Measure NOX at the exhaust of the stationary internal combustion engine; if using a control device, the sampling site must be located at the outlet of the control device. | (5) Method 7E of 40 CFR part 60, appendix A-4, ASTM Method D6522-00 (Reapproved 2005)ae, Method 320 of 40 CFR part 63, appendix A, or ASTM Method D 6348-03e | (d) Results of this test consist of the average of the three 1-hour or longer runs. |
|  | b. limit the concentration of CO in the stationary SI internal combustion engine exhaust. | i. Select the sampling port location and the number/location of traverse points at the exhaust of the stationary internal combustion engine; | (1) Method 1 or 1A of 40 CFR part 60, appendix A-1, if measuring flow rate | (a) Alternatively, for CO, O2, and moisture measurement, ducts ≤6 inches in diameter may be sampled at a single point located at the duct centroid and ducts >6 and ≤12 inches in diameter may be sampled at 3 traverse points located at 16.7, 50.0, and 83.3% of the measurement line ('3-point long line'). If the duct is >12 inches in diameter and the sampling port location meets the two and half-diameter criterion of Section 11.1.1 of Method 1 of 40 CFR part 60, Appendix A, the duct may be sampled at '3-point long line'; otherwise, conduct the stratification testing and select sampling points according to Section 8.1.2 of Method 7E of 40 CFR part 60, Appendix A. |
|  |  | ii. Determine the O2 concentration of the stationary internal combustion engine exhaust at the sampling port location; | (2) Method 3, 3A, or 3Bb of 40 CFR part 60, appendix A-2 or ASTM Method D6522-00 (Reapproved 2005)ae | (b) Measurements to determine O2 concentration must be made at the same time as the measurements for CO concentration. |
|  |  | iii. If necessary, determine the exhaust flowrate of the stationary internal combustion engine exhaust; | (3) Method 2 or 2C of 40 CFR part 60, appendix A-1 or Method 19 of 40 CFR part 60, appendix A-7 |  |
|  |  | iv. If necessary, measure moisture content of the stationary internal combustion engine exhaust at the sampling port location; and | (4) Method 4 of 40 CFR part 60, appendix A-3, Method 320 of 40 CFR part 63, appendix A, or ASTM Method D 6348-03e | (c) Measurements to determine moisture must be made at the same time as the measurement for CO concentration. |
|  |  | v. Measure CO at the exhaust of the stationary internal combustion engine; if using a control device, the sampling site must be located at the outlet of the control device. | (5) Method 10 of 40 CFR part 60, appendix A4, ASTM Method D6522-00 (Reapproved 2005)ae, Method 320 of 40 CFR part 63, appendix A, or ASTM Method D 6348-03e | (d) Results of this test consist of the average of the three 1-hour or longer runs. |
|  | c. limit the concentration of VOC in the stationary SI internal combustion engine exhaust | i. Select the sampling port location and the number/location of traverse points at the exhaust of the stationary internal combustion engine; | (1) Method 1 or 1A of 40 CFR part 60, appendix A-1, if measuring flow rate | (a) Alternatively, for VOC, O2, and moisture measurement, ducts ≤6 inches in diameter may be sampled at a single point located at the duct centroid and ducts >6 and ≤12 inches in diameter may be sampled at 3 traverse points located at 16.7, 50.0, and 83.3% of the measurement line (`3-point long line'). If the duct is >12 inches in diameter and the sampling port location meets the two and half-diameter criterion of Section 11.1.1 of Method 1 of 40 CFR part 60, Appendix A, the duct may be sampled at `3-point long line'; otherwise, conduct the stratification testing and select sampling points according to Section 8.1.2 of Method 7E of 40 CFR part 60, Appendix A. |
|  |  | ii. Determine the O2 concentration of the stationary internal combustion engine exhaust at the sampling port location; | (2) Method 3, 3A, or 3Bb of 40 CFR part 60, appendix A-2 or ASTM Method D6522-00 (Reapproved 2005)ae | (b) Measurements to determine O2 concentration must be made at the same time as the measurements for VOC concentration. |
|  |  | iii. If necessary, determine the exhaust flowrate of the stationary internal combustion engine exhaust; | (3) Method 2 or 2C of 40 CFR part 60, appendix A-1 or Method 19 of 40 CFR part 60, appendix A-7 |  |
|  |  | iv. If necessary, measure moisture content of the stationary internal combustion engine exhaust at the sampling port location; and | (4) Method 4 of 40 CFR part 60, appendix A-3, Method 320 of 40 CFR part 63, appendix A, or ASTM Method D 6348-03e | (c) Measurements to determine moisture must be made at the same time as the measurement for VOC concentration. |
|  |  | v. Measure VOC at the exhaust of the stationary internal combustion engine; if using a control device, the sampling site must be located at the outlet of the control device. | (5) Methods 25A and 18 of 40 CFR part 60, appendices A-6 and A-7, Method 25A with the use of a methane cutter as described in 40 CFR 1065.265, Method 18 of 40 CFR part 60, appendix A-6cd, Method 320 of 40 CFR part 63, appendix A, or ASTM Method D 6348-03e | (d) Results of this test consist of the average of the three 1-hour or longer runs. |

a	Also, you may petition the Administrator for approval to use alternative methods for portable analyzer.

b	You may use ASME PTC 19.10-1981, Flue and Exhaust Gas Analyses, for measuring the O2 content of the exhaust gas as an alternative to EPA Method 3B. AMSE PTC 19.10-1981 incorporated by reference, see 40 CFR 60.17

c	You may use EPA Method 18 of 40 CFR part 60, appendix A-6, provided that you conduct an adequate pre-survey test prior to the emissions test, such as the one described in OTM 11 on EPA's Web site (http://www.epa.gov/ttn/emc/prelim/otm11.pdf).

d	You may use ASTM D6420-99 (2004), Test Method for Determination of Gaseous Organic Compounds by Direct Interface Gas Chromatography/Mass Spectrometry as an alternative to EPA Method 18 for measuring total nonmethane organic hydrocarbons. ASTM D6420-99(2004) incorporated by reference; see 40 CFR 60.17.

e	Incorporated by reference; see 40 CFR 60.17.

- Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C]

{Permitting Note: Air compliance test notifications can now be completed online in the Department’s Business Portal.  To access this online process, go to http://www.fldepportal.com/go/home and sign in (or register if you’re a new user) from the link in the upper right corner of the page. On the Welcome page select the Submit option, then select Registration/Notification, and then click on Air Compliance Test Notifications.  Once in the process, just carefully read the instructions on each screen (and under the Help tabs) to complete the notification.}

Recordkeeping and Reporting Requirements

- The following records shall be kept for each engine:

  - All notifications submitted to comply with 40 CFR 60 Subpart JJJJ and all documentation supporting any notification.

- Maintenance conducted on the engine.

- Documentation that the engine meets the emission standards.

- The occurrence and duration of any routine startup event, routine shutdown event, breakdown condition or emergency situation.

[40 CFR 60.4245(a)(1),(2),(4); and Rule 62-204.800(8), F.A.C]

- Performance Test Report.  A copy of each performance test as conducted in Specific Condition B.14. shall be submitted to the Compliance Authority within 45 days after the test has been completed.

[40 CFR 60.4245(d); Rule 62-297.310(10), F.A.C; and Rule 62-204.800(8), F.A.C]

- Monitoring, Reporting and Recordkeeping Requirements.  To demonstrate that the post project actual annual emissions are equal to or less than the projected actual emissions of CO (142 tons/year), NOx (59.1 tons/year), SO2 (70.5 tons/year) and VOC (51.0 tons/year) for the 1.2 MW Digester Gas Electric Co-generators (EUs 021, 022, 024, and 025) in Permit No. 0250476-013-AC, the permittee shall do the following:

- The permittee shall monitor the pollutant emissions; and, using the most reliable information available, calculate and maintain a record of the annual emissions, in tons per year on a calendar year basis, for a period of 5 years following resumption of regular operations. Emissions shall be computed in accordance with Rule 62-210.370, F.A.C.

- The permittee shall report to the Department’s Office of Permitting and Compliance within 60 days after the end of each year during which records shall be generated under subparagraph 62-212.300(1)(e)1., F.A.C., setting out the units annual emissions during the calendar year that preceded submission of the report. The report shall contain the following:

- The name, address and telephone number of the Permittee of the major stationary source;

- The annual emissions as calculated pursuant to subparagraph 62-212.300(1)(e)1., F.A.C.;

- If the emissions differ from the preconstruction projection, an explanation as to why there is a difference; and

- Any other information that the Permittee wishes to include in the report.

- Reporting of any actual emissions levels that results in a significant increase of any pollutant as described in the Technical Evaluation and Preliminary Determination document for this project shall require that the permittee submit a PSD air construction permit application to address the pollution increase.

- The information required to be documented and maintained pursuant to subparagraphs 62-212.300(1)(e)1. and 2., F.A.C., shall be submitted to the Department’s Office of Permitting and Compliance, which shall make it available for review to the general public.

[Rule 62-212.300 F.A.C.; and Permit No. 0250749-013-AC]

- Other Reporting Requirements. See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.

[Rule 62-213.440(1)(b), F.A.C.]

Table of Contents

The specific conditions in this section apply to the following emissions unit:

| EU No. | Brief Description |
| --- | --- |
| 023 | Diesel engine driven starting air compressor |

| E.U. ID No. | Engine Brake HP | Date of Construction | Primary Fuel | Type of Engine | Displacement liters/cylinder (l/c) | Manufacturer |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | Model # |
| 023 | 37.7 | 6-1-2000 | Ultra Low Diesel No. 2 | Non-Emergency | <10 | Hatz Diesel of America, Inc. |
|  |  |  |  |  |  | 2M40LZ |

{Permitting Note: This emissions unit, compression ignition (CI) engine, is regulated under 40 CFR 63, Subpart ZZZZ, NESHAP for Stationary RICE adopted in Rule 62.204.800(11)(b), F.A.C.  This RICE is regulated as an existing non-emergency engine less than or equal to 300 HP that is located at an area source of HAPs and that has not been modified or reconstructed after 6/12/2006.  If the RICE is modified or reconstructed after 7/11/2005, the NSPS 40 CFR 60, Subpart IIII, will then apply.}

{Permitting Note: During the next Title V renewal or air construction permit modification, whichever comes first, the facility-wide potential individual (i.e., formaldehyde, etc.) and total HAP emissions need to be provided by the facility in the submitted permit application.}

Essential Potential to Emit (PTE) Parameters

- Engine Startup.  During periods of startup the Permittee shall minimize the engine's time spent at idle and minimize the engine's startup time to a period needed for the appropriate and safe loading of the engine, not to exceed 30 minutes, after which time the non-startup emission limitations in Specific Condition C.2. apply.

[40 CFR 63.6625(h); and Rule 62.204.800(11)(b)82., F.A.C.]

Emission Limitations and Standards

- Work or Management Practice Standards.

  - Oil. Change oil and filter every 1000 hours of operation or annually, whichever comes first.  [40 CFR 63.6603(a) & Table 2d1.a.]

  - Air Cleaner.  Inspect air cleaner every 1,000 hours of operation or annually, whichever comes first.  [40 CFR 63.6603(a) & Table 2d1.b.]

  - Hoses and Belts.  Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary.  [40 CFR 63.6603(a) & Table 2d1.c.]

  - Operation and Maintenance.  Operate and maintain the stationary RICE according to the manufacturer's emission-related operation and maintenance instructions or develop and follow your own maintenance plan which shall provide, to the extent practicable for the maintenance and operation of the engine in a manner consistent with good air pollution, control practice for minimizing emissions.  [40 CFR 63.6625(e), 63.6640(a) & Table 6.9.a.]

  - Oil Analysis. The Permittee has the option of using oil analysis to extend the change requirement.  The oil analysis shall be performed at the same frequency specified for changing the oil in Specific Condition C.2.a. The analysis program shall at a minimum analyze the following three parameters:  Total Base Number, viscosity, and percent of water content.  The condemning limits for these parameters are as follows: Total Base Number is less than 30 percent of the Total Base Number of the oil when new; viscosity of the oil has changed by more than 20 percent from the viscosity of the oil when new; or percent of water content (by volume) is greater than 0.5.  If all of these condemning limits are not exceeded, the engine Permittee is not required to change the oil.  If any of the limits are exceeded, the engine Permittee shall change the oil within 2 days of receiving the results of the analysis; if the engine is not in operation when the results of the analysis are received, the engine Permittee shall change the oil within 2 days or before commencing operation, whichever is later.  The Permittee shall keep records of the parameters that are analyzed as part of the program, the results of the analysis, and the oil changes for the engine.  The analysis program shall be part of the maintenance plan for the engine.  [40 CFR 63.6625(i); and Rule 62.204.800(11)(b)82., F.A.C.]

Compliance

- Continuous Compliance.  At all times, this unit:

- Shall be in compliance with the operating limitations.

- Shall be operated and maintained in a manner consistent with safety and good air pollution control practices for minimizing emissions. The general duty to minimize emissions does not require you to make any further efforts to reduce emissions if levels required by this standard have been achieved. Determination of whether such operation and maintenance procedures are being used will be based on information available to the Administrator which may include, but is not limited to, monitoring results, review of operation and maintenance procedures, review of operation and maintenance records, and inspection of the source.

[40 CFR 63.6605; and Rule 62.204.800(11)(b)82., F.A.C.]

Recordkeeping Requirements

- Records. The Permittee shall keep the records described in this Specific Condition:

  - A copy of each notification and report that is submitted, including all documentation supporting any Initial Notification or Notification of Compliance Status that is submitted according to the requirement in 40 CFR 63.10(b)(2)(xiv).

  - Records of the occurrence and duration of each malfunction of operation (i.e., process equipment) or the air pollution control and monitoring equipment.

  - Records of all required maintenance performed on the air pollution control and monitoring equipment.

  - Records of actions taken during periods of malfunction to minimize emissions in accordance with Specific Condition C.3.b., including corrective actions to restore malfunctioning process and air pollution control and monitoring equipment to its normal or usual manner of operation.

[40 CFR 63.6655(a)(1),(2),(4),(5), Rule 62-204.800(11)(b)82., F.A.C.]

- Records. The Permittee shall keep the records required in Table 6 of 40 CFR 63 Subpart ZZZZ (stated in Specific Condition C.2.d.) to show continuous compliance with each emission or operating limitation stated in Specific Condition C.2.

[40 CFR 63.6655(d); and Rule 62-204.800(11)(b)82., F.A.C.]

- Maintenance Records.  The Permittee shall keep records of the maintenance conducted on this unit in order to demonstrate that it is operated and maintained according to their own maintenance plan.

[40 CFR 63.6655(e); and Rule 62.204.800(11)(b)82., F.A.C.]

- Record Retention.

- The Permittee shall keep records in a suitable and readily available form for expeditious reviews.

- The Permittee shall keep each record readily accessible in hard copy or electronic form for at least 5 years after the date of each occurrence, measurement, maintenance, corrective action, report, or record.

[40 CFR 63.6660; Rule 62.204.800(11)(b)82., F.A.C.; and 40 CFR 63.10(b)(1)]

- General Provisions.  Table 8 of 40 CFR 63 Subpart ZZZZ shows which parts of the General Provision are applicable.  The Permittee shall report each instance in which the requirements in Table 8 of 40 CFR 63 Subpart ZZZZ are not met. Refer to Appendix.

[40 CFR 63.6640(e); Rule 62-204.800(11)(b)82., F.A.C.; 40 CFR 63.6665; and Rule 62-204.800(11)(d)1., F.A.C.]

Table of Contents

The specific conditions in this section apply to the following emissions unit:

| EU No. | Brief Description |
| --- | --- |
| 027 | Gasoline Dispensing Facilities (GDF). A gasoline fuel dispensing facility managed by the Miami-Dade Internal Services Department for fueling of County and other municipal vehicles. |

{Permitting Note:  This EU is subject to 40 CFR 63 Subpart CCCCCC – Gasoline Dispensing Facilities (GDF)}

The GDF NESHAP regulates gasoline loading of storage tanks and applies to all GDF located at an area source.  A GDF is defined as a facility that dispenses gasoline into a fuel tank of a motor vehicle, which includes all retail gasoline stations and many fleet vehicle refueling centers.  This also includes facilities that dispense gasoline into on- and off-road street or highway motor vehicles, lawn equipment, boats, test engines, landscaping equipment, generators, pumps, and other gasoline-fueled engines and equipment.

The requirements in the NESHAP are based on the monthly average throughput of gasoline.

{Permitting Note: During the next Title V renewal or air construction permit modification, whichever comes first, the facility-wide potential individual (i.e., formaldehyde, etc.) and total HAP emissions need to be provided by the facility in the submitted permit application.}

- Gasoline Dispensing Facilities (GDF).  The affected source to which 40 CFR 63 Subpart CCCCCC applies is each GDF that is located at an area source.  The affected source includes each gasoline cargo tank during the delivery of product to a GDF and also includes each storage tank.

[40 CFR 63.11111(a)]

- Gasoline Dispensing Facilities (GDF).  GDF with a monthly throughput of less than 10,000 gallons of gasoline, the must comply with the requirements in 40 CFR 63.11116 (Specific Condition No. D.11.)

[40 CFR 63.11111(b)]

- Monthly Recordkeeping of Throughput.  The facility shall, upon request by the Department, demonstrate that their monthly throughput is less than the 10,000-gallon threshold level, as applicable.  Records required under this paragraph shall be kept for a period of 5 years.

[40 CFR 63.11111(e)]

- Monthly Throughput.  Monthly throughput is the total volume of gasoline loaded into, or dispensed from, all the gasoline storage tanks located at a single affected GDF.  If an area source has two or more GDF at separate locations within the area source, each GDF is treated as a separate affected source.

[40 CFR 63.11111(h)]

- Throughput exceeding an Applicable Throughput Threshold.  If your affected source's throughput ever exceeds an applicable throughput threshold, the affected source will remain subject to the requirements for sources above the threshold, even if the affected source throughput later falls below the applicable throughput threshold.

[40 CFR 63.11111(i)]

- Dispensing of Gasoline From a Fixed Storage Tank into a Portable Gasoline Tank. The dispensing of gasoline from a fixed gasoline storage tank at a GDF into a portable gasoline tank for the on-site delivery and subsequent dispensing of the gasoline into the fuel tank of a motor vehicle or other gasoline-fueled engine or equipment used within the area source is only subject to 40 CFR 63.11116 (Specific Condition No. D.11.).

[40 CFR 63.11111(j)]

- Applicable Emission Sources.  The emission sources to which 40 CFR 63 Subpart CCCCCC applies are gasoline storage tanks and associated equipment components in vapor or liquid gasoline service at the facility existing GDF that meet the criteria specified in 40 CFR 63.11111 (Specific Condition No. D.1. - D.6.).  Pressure/Vacuum vents on gasoline storage tanks and the equipment necessary to unload product from cargo tanks into the storage tanks at GDF are covered emission sources.  The equipment used for the refueling of motor vehicles is not covered by 40 CFR 63 Subpart CCCCCC.

[40 CFR 63.11112(a)]

- Existing Affected Source.  This source is an existing affected source.

[40 CFR 63.11112(d)]

- Control Requirements.  The facility must comply with the standards in 40 CFR 63, Subpart CCCCCC.

[40 CFR 63.11113(f); and 40 CFR 63.11116(c)]

- Emission Limitations and Management Practices. The Permittee shall comply with the requirements of paragraphs a. and b. of this Specific Condition.

- The facility must, at all times, operate and maintain any affected source, including associated air pollution control equipment and monitoring equipment, in a manner consistent with safety and good air pollution control practices for minimizing emissions.  Determination of whether such operation and maintenance procedures are being used will be based on information available to the Department which may include, but is not limited to, monitoring results, review of operation and maintenance procedures, review of operation and maintenance records, and inspection of the source.

- The facility must keep applicable records and submit reports as specified in 40 CFR 63.11125(d) (Specific Condition No. D.14.).

[40 CFR 63.11115(a) and (b)]

- Requirements for Facilities with Monthly Throughput of Less than 10,000 Gallons of Gasoline.  The facility shall not allow gasoline to be handled in a manner that would result in vapor releases to the atmosphere for extended periods of time.  Measures to be taken include, but are not limited to, the following:

  - Minimize gasoline spills;

  - Clean up spills as expeditiously as practicable;

  - Cover all open gasoline containers and all gasoline storage tank fill-pipes with a gasketed seal when not in use;

  - Minimize gasoline sent to open waste collection systems that collect and transport gasoline to reclamation and recycling devices, such as oil/water separators.

[40 CFR 63.11116(a)(1) – (4)]

- Notifications or Reports.  The facility is not required to submit notifications or reports as specified in 40 CFR 63.11125, or Subpart A of 40 CFR 63, Subpart CCCCCC, but must have records available within 24 hours of a request by the Department to document your gasoline throughput.

[40 CFR 63.11116(b)]

- Portable Gasoline Containers.  Portable gasoline containers that meet the requirements of 40 CFR part 59, subpart F, are considered acceptable for compliance with Specific Condition No. D.11.c.

[40 CFR 63.11116(d)]

- Recordkeeping.  The Permittee shall keep records as specified in this Specific Condition.

  - Records of the occurrence and duration of each malfunction of operation (i.e., process equipment) or the air pollution control and monitoring equipment.

  - (2) Records of actions taken during periods of malfunction to minimize emissions in accordance with 40 CFR 63.11115(a) (Specific Condition No. D.10.a.), including corrective actions to restore malfunctioning process and air pollution control and monitoring equipment to its normal or usual manner of operation.

[40 CFR 63.11125(d)(1) and (2)]

- Definitions.  This facility is subject to the definitions in 40 CFR 63, Subpart CCCCCC.

[40 CFR 63.11132]

- General Provisions.  Table 3 to 40 CFR 63, Subpart CCCCCC shows which parts of the General Provisions apply to this facility.

[40 CFR 63.11130]