## APPENDIX G
APPENDIX G
ON-SITE INSPECTION CHECKLISTS
The following checklists are provided in this appendix:
Monitoring Equipment
Recordkeeping
Collection and Control Equipment
ON-SITE INSPECTION CHECKLISTS
FOR DETERMINING COMPLIANCE WITH MSW LANDFILL NSPS AND EG
These checklists can be used to verify compliance with the NSPS or EG monitoring, recordkeeping, and control equipment requirements. Inspectors should use copies of these checklists for each inspection.
A "yes" response to checklist questions indicates compliance with the regulations. A "no" response does not necessarily indicate non-compliance. The inspector has the discretion to determine compliance or non-compliance. Therefore, the inspector should determine if the intent of the requirements has been achieved. In the case of a "no" response, indicate whether the checklist question, and hence the requirement, is satisfied. | [5 empty] | 2009-04-07
Inspector: Art Pennetta - Broward County
MONITORING EQUIPMENT CHECKLIST
Refer to each appropriate section below to determine compliance with monitoring requirements of the rule. Complete the checklist by indicating "yes" or "no" to the questions. A "yes" indicates compliance. A "no" does not necessarily indicate non-compliance with the regulations.
NA indicates that the checklist item is not applicable to this site. After completing the checklist, press the following button to hide all the questions that are not applicable. This will leave only the questions marked Yes or No, and those not marked at all. This page can be saved to your computer any time, but it will not be uploaded to Inspection History unless every question has had Yes, No or NA selected.
ACTIVE GAS COLLECTION SYSTEMS [§60.756(a)] | [5 empty] | COMMENTS:
Yes | No | NA
Yes | No | NA
|  | FALSE | 1 | Is a sampling port installed at each wellhead?
|  | FALSE | 2 | Is there a thermometer, other temperature measuring device, or an access port for temperature measurements at each wellhead?
|  |  | 3 | Are the following parameters being monitored?
|  | FALSE |  | • | gauge pressure in the gas collection header on a monthly basis
|  | FALSE |  | • | nitrogen concentration in the landfill gas as provided in Method 3C or oxygen concentration as provided in Method 3A
|  | FALSE |  | • | temperature of the landfill gas on a monthly basis
|  | TRUE | 4 | If an alternative method is used to monitor for infiltration, is this method documented and maintained with the landfill records?
ENCLOSED COMBUSTION DEVICES [§60.756(b)]
Yes | No | NA
|  |  | 1 | Is the following required equipment being calibrated, maintained, and operated according to the manufacturer's specifications?
|  |  |  | • | a temperature monitoring device equipped with a continuous recorder and having an accuracy of ±1 percent of the temperature being measured, expressed in degrees Celsius or ±0.5 °C, whichever is greater (except when the control device is a boiler or process heater >44 megawatts)
|  |  |  | • | a gas flow measuring device that records the gas flow to the control device or bypass lines are sealed shut and seals are inspected monthly
|  |  | 2 | Are the temperature and the gas flow (if applicable) being recorded at least every 15 minutes?
OPEN FLARES [§60.756(c)]
Yes | No | NA
|  |  | 1 | Is the following required equipment being calibrated, maintained, and operated according to the manufacturer's specifications?
|  |  |  | • | a heat sensing device, such as an ultraviolet beam sensor or thermocouple, at the pilot light or at the flare flame to indicate the continuous presence of a flame
|  |  |  | • | a device that records the gas flow to or bypass of the flare or bypass lines are sealed shut and seals are inspected monthly
|  |  | 2 | Are the presence of the pilot light and the gas flow (if applicable) being recorded at least every 15 minutes?
OTHER CONTROL DEVICES [§60.756(d) and §60.756(e)]
A. | OTHER CONTROL DEVICES
Yes | No | NA
|  |  | 1 | If a control device other than a flare or enclosed combustion device is used, does the landfill have documentation demonstrating that the alternative device was approved by the Administrator?
|  |  | 2 | If the Administrator specified additional monitoring procedures, does the landfill have appropriate records demonstrating compliance with these procedures?
B. | COLLECTION SYSTEMS NOT CONFORMING TO §60.759
|  |  | 1 | If a collection system not conforming to §60.759 is used, does the landfill have documentation demonstrating that the alternative design was approved by the Administrator?
|  |  | 2 | If the Administrator specified additional monitoring procedures, does the landfill have appropriate records demonstrating compliance with these procedures?
MONITORING METHANE CONCENTRATIONS AT THE LANDFILL SURFACE [§60.756(f)]
Yes | No | NA
|  |  | 1 | Are surface concentrations of methane being monitored on a quarterly basis to determine compliance (unless the skip period method described in #3 below is used)?
|  |  | 2 | Does the monitoring device comply with the following instrumentation specifications and procedures for surface emission monitoring devices [§60.755(d)]:
|  |  |  | • | Does the portable analyzer meet the instrument specifications in Section 3 of Method 21, except that "methane" replaces all references to VOC?
|  |  |  | • | Is the calibration gas methane, diluted to a nominal concentration of 500 ppm in air?
|  |  |  | • | To meet the performance evaluation requirements in Section 3.1.3 of Method 21, are the instrument evaluation procedures of Section 4.4 of the method used?
|  |  |  | • | Are the calibration procedures provided in Section 4.2 of Method 21 followed immediately before commencing a surface monitoring survey?
|  |  | 3 | Are the following procedures, provided in §60.756(f), followed if skip period monitoring is used:
|  |  |  | • | If no exceedances are detected for three successive quarterly monitoring periods, is the surface monitored annually until an exceedance is detected?
|  |  |  | • | If an exceedance is detected and corrected as provided in §60.755(a)(5), is the surface monitored quarterly until a concentration >500 ppm is not detected for three successive quarters?
RECORDKEEPING CHECKLIST
Refer to each appropriate section below to determine compliance with the recording requirements of the rule. A "yes" indicates compliance. A "no" does not necessarily indicate non-compliance with the regulations.
GENERAL RETENTION REQUIREMENTS [§60.758(a)]
Yes | No | NA
|  |  | 1 | Are all records
|  |  |  | • | available for at least the past 5 years?
|  |  |  | • | up-to-date?
|  |  |  | • | readily accessible?
|  |  |  | • | on-site or, if offsite, retrievable in 4 hours?
|  |  |  | • | in hardcopy or electronic format?
|  |  | 2 | Are records of the following information available?
|  |  |  | • | maximum design capacity
|  |  |  | • | current amount of MSW in place
|  |  |  | • | year-by-year waste acceptance rate
INITIAL PERFORMANCE TEST OR COMPLIANCE DETERMINATION FOR CONTROL EQUIPMENT [§60.758(b)]
Yes | No | NA
|  |  | 1 | Are records that document the initial performance test or compliance determination kept for the life of the control equipment?
|  |  | 2 | Are records of any subsequent compliance tests or compliance determinations maintained for at least 5 years?
|  |  | 3 | Do the records include the following information?
|  |  |  | • | the density of wells is sufficient as calculated by procedures in §60.759(a)(1), and
|  |  |  | • | the maximum expected gas generation flow rate as calculated by the procedure in §60.755(a)(1); or
|  |  |  | • | the maximum expected gas generation flow rate as calculated by another approved method.
|  |  | 4 | For owners or operators using enclosed combustion devices other than boilers and process heaters, do the records include the following?
|  |  |  | • | average combustion temperature measured at least every 15 minutes and averaged over the same time period as the performance test
|  |  |  | • | a percent reduction of 98 percent or greater, or an NMOC concentration less than 20 ppm by volume, dry basis as hexane at 3% oxygen
|  |  | 5a. | For owners or operators using any size boiler or process heater, do the records include the following?
|  |  |  | • | description of the location at which the collected gas vent stream is introduced into the boiler or process heater over the same time period of the performance testing
|  |  | 5b. | For owners or operators using boilers or process heaters with a design heat input capacity of less than 44 megawatts, do the records include the following?
|  |  |  | • | the average combustion temperature of the boiler or process heater measured at least every 15 minutes and averaged over the same time period of the performance testing
|  |  |  | • | a percent reduction of 98 percent or greater or an NMOC concentration less than 20 ppm by volume, dry basis as hexane at 3 percent oxygen
|  |  | 6 | For owners or operators using an open flare, do the records include the following?
|  |  |  | • | flare type (i.e., steam assisted, air-assisted, or nonassisted)
|  |  |  | • | all visible emission readings
|  |  |  | • | heat content determinations
|  |  |  | • | flow or bypass flow records
|  |  |  | • | exit velocity determinations
|  |  |  | • | continuous records of the flare flame or pilot flame monitoring
|  |  |  | • | records of all periods of operation during which the pilot flame or flare flame was absent
|  |  | 7 | For owners or operators using a flare, do the visible emission, heat content, flow rate, and exit velocity data show that specifications in §60.18 are met? (The specifications vary by flare type.)
EQUIPMENT OPERATING PARAMETERS AND PARAMETER BOUNDARY EXCEEDANCES [§60.758(c)]
Yes | No | NA
|  |  | 1 | Are records available of all equipment operating parameters and parameter boundary exceedances?
|  |  | 2 | Are the records retained for at least 5 years?
|  |  | 3 | Are the records continuous (i.e., a value recorded at least every 15 minutes)?
|  |  | 4 | For enclosed combustion devices (except for boilers and process heaters with design heat input capacity of 44 megawatts or greater and open flares), were all 3-hour periods of operation during which the average combustion temperature was more than 28°C below the average combustion temperature during the most recent performance test recorded and reported?
|  |  | 5 | For all boilers and process heaters, were any changes in location at which the vent stream was introduced into the flame zone recorded and reported?
|  |  | 6 | For all control devices,
|  |  |  | • | were continuous records of LFG flow to the control device or bypass flow maintained or, if bypass lines were sealed closed, were monthly seal inspection results recorded?
|  |  |  | • | were all periods when the gas stream was diverted from the control device or had no flowrate recorded and reported?
|  |  | 7 | For owners or operators using a boiler or process heater with a design input capacity of 44 megawatts or greater, are records of all periods of operation of the boiler or process heater available?
|  |  | 8 | For owners or operators using an open flare:
|  |  |  | • | were continuous records maintained of pilot flame or flare flame monitoring?
|  |  |  | • | were all periods of operation in which the flare or pilot flame was absent recorded and reported?
COLLECTION SYSTEM INFORMATION [§60.758(d)]
Yes | No | NA
|  |  | 1 | Is an up-to-date, readily accessible collection system plot map available?
|  |  | 2 | Does the plot map include the following?
|  |  |  | • | the location of each existing and planned collector in the system
|  |  |  | • | a unique identification label for each collector
|  |  | 3 | Did the well records include the following information related to newly installed collectors?
|  |  |  | • | installation date of each collector
|  |  |  | • | location of each collector
WASTE EXCLUDED FROM COLLECTION - AREAS INCLUDED IN THE 1 PERCENT THAT DO NOT WARRANT CONTROL [§60.758(d)]
Yes | No | NA
|  |  | 1 | Do the records pertaining to asbestos-containing or nondegradable waste excluded from collection and/or any area included in the 1 percent that does not warrant control include the following?
|  |  |  | • | nature of the waste
|  |  |  | • | date of deposition of the waste
|  |  |  | • | amount of the waste
|  |  |  | • | location of waste on the landfill site
COLLECTION AND CONTROL EXCEEDANCE [§60.758(e)]
Yes | No | NA
|  |  | 1 | Are records of the following available:
|  |  |  | • | all collection and control system exceedances of the operational standards in §60.753? These include: readings of positive pressure at any wellhead (except as allowed in §60.753(b); wellhead temperature >55°C or other approved temperature; nitrogen level ≥20% or oxygen level ≥5%; and surface methane concentration ≥500 ppm
|  |  |  | • | a reading in the month following an exceedance
|  |  |  | • | location of each exceedance
DESIGN CAPACITY CALCULATION [§60.758(f)]
Yes | No | NA
|  |  | 1 | For landfill owners or operators who convert design capacity from volume to mass or from mass to volume to demonstrate that landfill design capacity is less than the design capacity size limit, do the records include the annual recalculation of site-specific density, design capacity, and all supporting documentation?
COLLECTION AND CONTROL EQUIPMENT CHECKLIST
This checklist is to be used for collection and control systems that conform to the specifications provided in §60.759. If an alternative collection and control system was installed, the approved alternative design plans should be used to check for compliance. Complete the checklist by indicating "yes" or "no" to the questions. A "yes" indicates compliance. A "no" does not necessarily indicate non-compliance with the regulations.
SITING ACTIVE COLLECTION SYSTEMS [§60.759(a)]
Yes | No | NA
|  |  | 1 | Are the active collection wells sited throughout all gas producing areas of the landfill (that are at least 5 years old for active areas or 2 years old for areas that are closed or at final grade)?
|  |  | 2 | Is sufficient density of collectors demonstrated? (Sufficient density means any number, spacing, and combination of collection system components, including vertical wells, horizontal collectors, and surface collectors, necessary to maintain emission and migration control as determined by measures of performance.)
|  |  | 3 | If gas is not collected from any areas because they contain asbestos or nondegradable material, is the nature, date of deposition, location, and amount of asbestos or nondegradable material documented?
|  |  | 4 | If gas is not collected from nonproductive areas, has it been demonstrated that total emissions from the excluded areas are <1% of total NMOC emissions from the landfill?
|  |  | 5 | If gas is not collected from nonproductive areas, has the amount, location, and age of the material been documented?
CONSTRUCTION OF ACTIVE COLLECTION SYSTEMS [§60.759(b)]
Yes | No | NA
|  |  | 1 | Does the connector assembly used to connect the wellhead to the collection header pipes include the following:
|  |  |  | • | positive closing throttle valve,
|  |  |  | • | any necessary seals and couplings,
|  |  |  | • | access couplings,
|  |  |  | • | at least one sampling port?
|  |  | 2 | Are the landfill gas extraction components constructed of one of the following? (Check material used)
|  |  |  | • | polyvinyl chloride (PVC)
|  |  |  | • | high density polyethylene (HDPE) pipe
|  |  |  | • | fiberglass
|  |  |  | • | stainless steel
|  |  |  | • | other nonporous, corrosion-resistant material
|  |  | 3 | Is the collection device constructed of one of the following? (Check material used.)
|  |  |  | • | PVC
|  |  |  | • | HDPE
|  |  |  | • | fiberglass
|  |  |  | • | stainless steel
|  |  |  | • | other nonporous material of suitable thickness _______
|  |  | 4 | Does the construction and location of wells and other collection system components match the approved collection and control system design plan?
GAS MOVER EQUIPMENT [§60.759(c)]
Yes | No | NA
|  |  | 1 | Is the gas mover equipment operating?
|  |  | 2 | Is the gas mover equipment sized to handle the maximum gas generation flow rate expected over the intended use period?
|  |  | 3 | Has the gas mover equipment exceeded its intended use period?
(The intended use period of the equipment should be specified in the approved collection and control system design plan.)