INSPECTION NOTES—2003

Solutia Inc.Solutia Inc.

Pensacola PlantPensacola Plant

Facility ID No.: 03300400330040

EscambiaEscambia County

FINAL Permit No.:  0330040-002-AV

Effective Date:  October 30, 2000

Renewal Application Due Date:  May 4, 2005

Expiration Date:  October 30, 2005

Section I.  Facility Information.

Subsection A.  Facility Description.

Solutia makes nylon and various intermediate chemicals.  This facility consists of several raw materials barge, train and truck offloading and storage operations; chemical unit process plants which make the chemical feedstocks and intermediates and the nylon resins; a yarn plant to make finished yarn product; and, boilers and a cogeneration unit to provide process steam and plant electricity.  Solutia also operates a maleic anhydride facility, which is not part of the nylon process.  The maleic anhydride facility is owned by Huntsman.

Based on the initial Title V permit application received June 12, 1996June 12, 1996, this facility is a major source of hazardous air pollutants (HAPs) and criteria pollutants.

Subsection B.  Summary of Emissions Unit ID Nos. and Brief Descriptions.

| Sub section | E.U. ID No. | Brief Description |
| --- | --- | --- |
| A | 014 | Boiler 4 |
| A | 015 | Boiler 5 |
| A | 016 | Boiler 6 |
| B | 003 | Boiler 8 |
| B | 004 | Boiler 7 |
| C | 076 | Maleic Anhydride (MA) Plant |
| D | 032 | Cogeneration Plant |
| E | 060 | Adipic Acid 485 BEPEX Dryer |
| E | 061 | Adipic Acid Dryer 405-A |
| E | 062 | Adipic Acid Dryer 405-B |
| E | 063 | Adipic Acid Dryer 465-A |
| E | 064 | Adipic Acid Dryer 465-B |
| E | 079 | Adipic Acid 485 NIRO Dryer |
| F | 002 | Adipic Acid Process |
| F | 090 | Adipic Acid Process- Fugitive Emissions |
| G | 005 | Vaporizer No.1 |
| G | 007 | Vaporizer No.2 |
| G | 008 | Vaporizer No.3 |
| G | 009 | Vaporizer No.4 |
| G | 010 | Vaporizer No.5 |
| G | 011 | Vaporizer No.6 |
| G | 013 | Vaporizer No.7 |
| G | 075 | Vaporizer No.8 |
| H | 081 | Continuous Nylon Polymerization LinesContinuous and Batch Polymerization Processes Modifications |
| H | 082 | Batch Nylon Polymerization |
| I | 020 | Cyclohexane Oxidation Process |
| J | 049 | Hydrogen Generating Plant #1 |
| K | 040 | Hexamethylene Diamine Synthesis and Refining |
| K | 041 | B and C Hexamethylene Diamine Stripper Distillation Column |
| L | 042 | Nitric Acid PlantContinuous and Batch Polymerization Processes Modifications |
| M | 088 | Area 480 KA Expansion |
| M | 089 | Area 480 KA Expansion- Fugitive Emissions |
| N | 097 | NSPS Storage Tanks |

Unregulated Emissions Units and/or Activities

| E.U. ID No. | Brief Description of Emissions Units and/or Activity |
| --- | --- |
| 073 | Abrasive Blast Facility |
| 038 | Research and Development |
| 050 | Adipic Acid Bulk Loading No. 1, Building 346 |

SECTION II,  FACILITY-WIDE CONDITIONS.

The following conditions apply facility-wide:

1.  APPENDIX TV-3, TITLE V CONDITIONS, is a part of this permit.

2.  General Pollutant Emission Limiting Standards. Objectionable Odor Prohibited.  The permittee shall not cause, suffer, allow, or permit the discharge of air pollutants, which cause or contribute to an objectionable odor.

3.  General Particulate Emission Limiting Standards.  General Visible Emissions Standard.  Except for emissions units that are subject to a particulate matter or opacity limit set forth or established by rule and reflected by conditions in this permit, no person shall cause, let, permit, suffer or allow to be discharged into the atmosphere the emissions of air pollutants from any activity, the density of which is equal to or greater than that designated as Number 1 on the Ringelmann Chart (20 percent opacity).  EPA Method 9 is the method of compliance pursuant to Chapter 62-297, F.A.C.

4.  Prevention of Accidental Releases (Section 112(r) of CAA).

a.  As required by rule, inspection, or change in process the owner or operator shall submit an updated Risk Management Plan (RMP) to the Chemical Emergency Preparedness and Prevention Office (CEPPO) RMP Reporting Center.

b.  The owner or operator shall report to the Department of Community Affairs (DCA) within one working day of discovery of an accidental release of a regulated substance from the stationary source, if the owner or operator is required to report the release to the USEPA/Chemical Safety Hazard Investigation Board or the National Response Center under Section 112(r)(6).

c.  The owner or operator shall submit the required annual registration fee to the DCA on or before April 1 annually, in accordance with Part IV, Chapter 252, F.S. and Rule 9G-21, F.A.C.

5.  General Pollutant Emission Limiting Standards. Volatile Organic Compounds (VOC) Emissions or Organic Solvents (OS) Emissions.  The permittee shall allow no person to store, pump, handle, process, load, unload or use in any process or installation, volatile organic compounds (VOC) or organic solvents (OS) without applying known and existing vapor emission control devices or systems deemed necessary and ordered by the Department.

6.  Reasonable precautions to prevent emissions of unconfined particulate matter at this facility include the application of good housekeeping practices.

7.  When appropriate, any recording, monitoring, or reporting requirements that are time-specific shall be in accordance with the effective date of the permit, which defines day one.

- The permittee shall submit all compliance related notifications and reports required of this permit to the Department’s Northwest District office:

- Any reports, data, notifications, certifications, and requests required to be sent to the United States Environmental Protection Agency, Region 4, should be sent to:

- Unless otherwise specified by rule or specific condition, permittee shall maintain 95% data capture and collection of monitoring data for recordkeeping purposes, on an annual basis. This management practice objective is based on an allowance of no more than 5% loss of data due to monitor downtime or loss of data capture due to other causes.

SECTION III, EMISSIONS UNITS AND  CONDITONS

AREA VI—POWERHOUSE

### Solutia Representatives:  Warren Whitfield, Jeff Harmon and Michael Grissett

Subsection A.  This section addresses the following emissions units.

| E.U. ID No. | Brief Description |
| --- | --- |
| 014 | Boiler 4 Not operating at the time of the inspection. |
| 015 | Boiler 5 |
| 016 | Boiler 6 |

These boilers are normally fueled by natural gas and ethane rich natural gas.  No. 6 fuel oil is an alternate fuel which may contain blended on-specification used oil as supplemental fuel.  The used oil must meet the requirments of 40 CFR Part 279 - Standards for the Management of Used Oil.  Boilers 4 and/or 5 may also burn as supplemental fuels AGS (a mixture of organic acids from deep well waste stream), KATT (a mixture of organic esters), DME (Dimethyl Esters), Amines and Area 480 residue.  Emissions are controlled by proper combustion control and by fuel composition.

These emissions units are regulated under Rules 62-296.405 (SO2 aggregate) and 62-296.406 F.A.C., Fossil Fuel Steam Generators with less than 250 MMBtu heat input.

The following specific conditions apply to the emissions unit(s) listed above:

Essential Potential to Emit (PTE) Parameters

A.1.  Capacity.  The aggregate maximum operating rate is 723 MMBtu per hour for Boilers 4, 5 and 6 with no individual boiler limits. During periods of outage of the cogeneration, boilers 4, 5 and 6 may operate at a combined maximum operating rate of 864 MMBtu per hour.  Records of heat input shall be maintained and made available for Department inspection.

*COMPLIANCE ISSUE.  Records: Y-T-D records indicate compliance with the permitted conditions except on 3/10/03 the aggregate maximum operating rate of 723 MMBtu/hr was exceeded while the Cogen was on line.  The rates on Boilers 4, 5 and 6 had been increased due to the shutdown of Boiler 8.  The excursion lasted for 2 hours.

Solutia discovered the excursion during a self-audit and reported it on 8/19/03 and it was reported in the Semiannual Monitoring Report.  Solutia took the following action to prevent reoccurrence:

- Posted visual aids to serve as reminders for all permit limits in the Powerhouse control room.

- Provided refresher training of Title V permit limits and updated operating instructions to place emphasis on Title V condition A.1.

- Installed an alarm to prevent exceedances of the maximum aggregate operating rate.

The Department considers the actions taken by Solutia sufficient.

A.2.  Methods of Operation - Fuels.  These boilers may be fueled by natural gas or ethane rich natural gas.  No. 6 fuel oil, blended with on-specification used oil, may be used as an alternate fuel provided the Department is notified in writing within seven days of the fuel change over.  If fuel oil use exceeds six hours per day on each of four or more days within a 30-day period, a visible emission compliance test shall be conducted within 14 days using the maximum quantity of fuel oil.  Testing is not required if a passing test has been successfully conducted within the last 12 months.

Fired:  VE testing was completed 3/3/03.

Used Oil.  Burning of on-specification used oil is allowed in this emissions unit in accordance with all other conditions of this permit and the following conditions:

On-specification Used Oil Emissions Limitations:  This emissions unit is permitted to burn on-specification used oil.  On-specification used oil is defined as used oil that meets the specifications of 40 CFR 279 - Standards for the Management of Used Oil, listed below. The owner shall maintain records to demonstrate that each shipment of used oil meets the specifications of 40 CFR 279.  “Off-specification” used oil shall not be burned. Used oil, which fails to comply with any of these specification levels, is considered “off-specification” used oil.

|  | CONSTITUENT/property | ALLOWABLE LEVEL |
| --- | --- | --- |
|  | Arsenic | 5 ppm maximum |
|  | Cadmium | 2 ppm maximum |
|  | Chromium | 10 ppm maximum |
|  | Lead | 100 ppm maximum |
|  | Total Halogens | 1000 ppm maximum |
|  | Flash point | 100 degrees F minimum |

Used oil is not burned in these boilers.

Supplemental Fuels.  The following supplemental fuels may be burned in boilers 4 and/or 5 in conjunction with burning of gas or fuel oil:

1.  AGS, a mixture of organic acids extracted from the deep well waste stream, up to 8,000 pounds per hour, and/or

2.  KATT composite fuel, consisting of KATT (Ketone Alcohol Topper Tails), DME (mixture of Dimethyl Esters), Amines (from nylon and nylon intermediates manufacturing) and Area 480 residue (a mixture of alcohol and ketone by-products) up to 10,000 pounds per hour.

* COMPLIANCE ISSUE.  Excessive KATT was burned for 15 hours on April 24 and 25, 2003.  Solutia discovered the excursion during a self-audit and reported it on 8/19/03 and it was reported in the Semiannual Monitoring Report.  The facility took the following actions to prevent reoccurance:

- Posted visual aids to serve as reminders for all permit limits in the Powerhouse control room.

- Provided refresher training of Title V permit limits and updated operating instructions to place emphasis on Title V condition A.2.

- Installed an alarm to prevent exceedances of the maximum KATT feed rate.

3.  These fuels may only be burned in Boiler 4 and/or 5.  Records shall be maintained of the supplemental fuel quantities burned.  A request may be made by the Department to periodically sample and analyze supplemental fuels.  The supplemental fuels shall be sampled and results submitted with the application for renewal of this permit.

Review Records: Y-T-D records contain the type and quantity of fuel burned in these boilers is maintained.

Emission Limitations and Standards

A.3.  Visible emissions shall not exceed 20% opacity except for up to two minutes in any one hour at not more than 40% opacity.

No excess emissions were noted from normal operating conditions or during soot blowing.

A.4.	Sulfur Dioxide.   The aggregate maximum total sulfur dioxide emissions from boilers 4, 5 and 6 shall be less than 57.5 tons in any 24-hour period.  Monthly records of sulfur dioxide emissions, based on fuel usage and sulfur content, shall be maintained and made available for inspection by the Department.

Y-T-D Records Review: Records are kept in a computer database and indicate compliance.  The highest daily sulfur emission was 23.5 tons.  The facility has determined that as long as a sulfur content of 5.9% by wt is maintained, the sulfur emissions will not be exceeded.  The records review showed a high of 2.98% by wt.

`

Test Methods and Procedures

A.5.  Emissions Tests.  See common condition number O.1.

| EU | Boiler | Result | Date |
| --- | --- | --- | --- |
| 014 | 4 | Passed | 3/12/03 |
| 015 | 5 | Passed | 3/12/03 |
| 016 | 6 | Passed | 3/12/03 |

A.6.  Visible Emissions.  EPA test method 9.

Testing above was done using Method 9.

A.7.  Determination of Process Variables.  See common condition number O.2.

Accuracy assured through periodic calibration by the instrument shop.

Periodic Monitoring

A.8.  Natural Gas Usage.  An aggregate natural gas usage heat input will be calculated on an hourly basis and recorded in units of MMBtu/hr for boilers 4, 5 and 6 combined.

Review records: These records are maintained.  Y-T-D records review shows one excursion.  See condition A.1.

A.9.  Supplemental Fuel Usage.  An aggregate supplemental fuel usage rate will be calculated on an hourly basis and recorded in units of lbs/hr for boilers 4 and 5 combined for each of the following supplemental fuel types

* KATT composite Fuel (KATT, Amines, DME residue, 480 residue)

* AGS

AGS is no longer used.  Y-T-D records review shows KATT fuel usage is maintained as required.  Excessive KATT was burned for 15 hours on April 24 and 25, 2003.

A.10.  Operation and Downtime Log.  An operation and downtime log will be maintained indicating the operational status of each of the boilers 4 through 8 and the cogeneration facility.

Review log.  A hand written log and database records the downtime and operating parameters.

A.11.  Sulfur Dioxide.  Monthly records of sulfur dioxide emissions, based on fuel usage and sulfur content, shall be maintained and made available for inspection by the Department.

Review  records.  These records are on hand.

Subsection B.  This section addresses the following emissions units.

| E.U. ID No. | Brief Description |
| --- | --- |
| 003 | Boiler 8 |
| 004 | Boiler 7 |

The boilers have been modified to incorporate low NOx burners and are fueled by natural gas, ethane rich natural gas, and Maleic Anhydride Production offgas.  Each of the modified burners are rated for 388 MMBtu/hour and 225,000 pounds/hour steam production. Emissions are controlled by proper combustion controls.  SO2 emissions are controlled by sulfur content of fuel.

These emissions units are regulated under Rule 62-296.405 F.A.C., Fossil Fuel Steam Generators with more than 250 MMBtu heat input; however, the emission limitations have been adjusted as a result of emission offsets associated with the facility’s cogeneration plant.

The following specific conditions apply to the emissions unit(s) listed above:

Essential Potential to Emit (PTE) Parameters

B.1.  Capacity.  The maximum operational heat input of each boiler is 388 MMBtu per hour. Heat input (MMBtu) is calculated using the previous year average natural gas fuel analysis provided by the vendor.  {Regular record keeping is not required for capacity limitations.}

B.2.  Methods of Operation - Fuels.  These boilers may be fueled by natural gas, ethane rich natural gas or Maleic Anhydride Production offgas.  The maximum total natural gas usage shall be limited to 1,100 million standard cubic feet per year for each boiler.  Records of monthly total and annual  total natural gas usage shall be maintained and available for Department inspection.

Records Review: As of 9/15/2003, Boiler 7 burned 667.4 MMscf and Boiler 4 burned  576.1 MMscf.  The projected trend keeps these boilers in compliance for the remainder of the year.

B.3.  Hours of Operation.  This emissions unit is allowed to operate continuously, i.e., 8,760 hours/year.

Emission Limitations and Standards

B.4.  Visible Emissions. Visible emissions shall not exceed 20% opacity except for up to one six-minute period per hour of up to 27%.

B.5.  Particulate Matter.   Particulate matter emissions from each unit shall not exceed 0.1 pounds per MMBtu.

B.6.  Carbon monoxide.  Carbon monoxide emissions from each unit shall not exceed 54.8 pounds per hour.

B.7.  Nitrogen oxides.  Nitrogen oxide emissions from each unit shall not exceed 22.5 pounds per hour.

B.8.  Volatile organic compounds.  Volatile organic compounds matter emissions from each unit shall not exceed 7.04 pounds per hour.

Test Methods and Procedures

B.9.  Emissions Tests.  See common condition number O.1.

B.10.  Visible Emissions.  EPA test method 9.

| EU | Boiler | Result | Date |
| --- | --- | --- | --- |
| 003 | 8 | Awaiting test report | 10/7/2003 |
| 004 | 7 | Awaiting test report | 09/42003 |

B.11.  Particulate Matter.  EPA test method 5:  Boilers 7 & 8 passed testing 8/22/02.  Boiler 7 was tested 9/4/03.  One run was excessively high causing a failed test.  Boiler & was retested 10/09/03.   Boiler 8 was tested 10/08/03.  Awaiting results of the tests.

B.12.  Carbon Monoxide.  EPA test method 10:  Boilers 7 & 8 passed testing in 2002.  Awaiting the results of the 2003 tests.

B.13.  Nitrogen Oxides.  EPA test method 7E.  Boilers 7 & 8 passed testing in 2002.  Awaiting the results of the 2003 tests.

* COMPLIANCE ISSUE`.  Stack test, RATA and VE were completed for Boiler 7 on 09/04/2004 and for Boiler 8 on 10/08/2003.  Boiler 7 exceeded the PM limit.  The first run had excessively high particulate matter results while the second and third runs were within permit limits.  But, the average of the three runs exceeded the permit limit.  It was retested 10/09/2003.  (awaiting results of these last two tests)

B.14.  Volatile Organic Compounds.  EPA test method 25A.  Testing is required only upon permit renewal.

B.15.  Determination of Process Variables.  See common condition number O.2.

### Accuracy is assured through scheduled calibration and PM.

Periodic Monitoring

B.16.   Continuous Emissions Monitoring. Permittee shall operate and maintain a carbon monoxide (CO) continuous emission monitor (CEM) on the exhaust stack for measurement of CO concentration. The CEM shall be properly operated and maintained to ensure accurate and reliable monitoring, recording, and reporting data.  Permittee shall implement and maintain a quality control program which, at a minimum, follows the quality assurance procedures set forth in 40 CFR 60 Appendix F, Quality Assurance Procedures, and Appendix B, Performance Specifications.  Such data may be used directly or indirectly for compliance determination. CO CEM data calculation is a rolling hourly average calculated every 15 minutes.  VOC and NOx compliance is assumed as long as CO CEMs data demonstrates compliance with the CO emission limit described in condition B.6.

Appendix F requirements for daily calibration checks, quarterly cylinder gas audits and relative accuracy audits are met.

B.17. Natural Gas Usage.  Natural gas usage heat input will be calculated on an hourly basis and reported in units of MMBtu/hr for boilers 7 and 8.

Records:  The records Y-T-D indicate compliance with this condition.

{Permitting note:  Records of maleic off-gas usage is a requirement of EU-076 condition C.6.}

Subsection D.  This section addresses the following emissions units.

| E.U. ID No. | Brief Description |
| --- | --- |
| 032 | Cogeneration Plant |

The cogeneration plant consists of one combustion turbine that exhausts through a heat recovery steam generator.  The heat recovery steam generator supplies steam to the manufacturing operations and replaces steam generated by the existing boilers.  The turbine, fueled by natural gas, turns a generator capable of producing a nominal 86 megawatts of electricity.  Supplemental firing of natural gas at the heat recovery steam generator will supply additional steam, if needed.  The combustion turbine employs steam injection to control NOx emissions.  Low NOx burner design is incorporated into the duct burner in conformance with 40 CFR 60 Subpart.  Operation of the combustion turbine using evaporative direct water spray fogging inlet air cooling is also authorized.

This emissions unit is regulated under applicable portions of NSPS - 40 CFR 60 Subparts A, Db and GG.

Essential Potential to Emit (PTE) Parameters.

D.1.  Capacity.  The maximum allowable heat input is 184 MMBtu per hour for the heat recovery steam generator duct burner.  The maximum allowable heat input for the combustion turbine varies with the ambient air temperature as specified in Table A-1, attached and incorporated by reference.  Table A-1 is used to determine rated capacity.  Ambient temperatures other than table values can be linearly interpolated or extrapolated.

*COMPLIANCE ISSUE:  Cogen exceeded maximum allowable heat input for the combustion turbine by 0.02% (0.18 MMBtu) on June 21, 2003 for 1 hour.  Solutia discovered the excursion during a self-audit and reported it on 8/19/03 and it was reported in the Semiannual Monitoring Report.  Solutia has provided an alarm system to alert operators when permit limit is approached.

D.2.  Methods of Operation.  This emissions unit shall be fueled by natural gas.

D.3.  Hours of Operation.  This emissions unit is allowed to operate continuously, i.e., 8,760 hours/year.

#### Emissions Limitations and Standards

D.4.   Visible emissions.  Visible emissions shall not exceed 20% opacity under normal operation except for up to one six-minute period per hour during which opacity shall not exceed 27% opacity.

Observed:  None observed at time of inspection.

D.5.  Total combined NOx emissions from the cogeneration plant turbine and duct burner shall not exceed 106.6 pounds per hour at the maximum allowable heat input rate for the combustion turbine (as specified in Table A-1) and the maximum allowable operating rate of 184 MMBtu/hr heat input for the duct burner.

D.6.  NOx emissions (expressed as NO2) from the duct burner, less emissions creditable to the combustion turbine, shall not exceed 0.2 pounds per million Btu, i.e., 36.8 pounds per hour at the maximum allowable operating rate of 184 MMBtu per hour heat input.

D.7.  Carbon monoxide.  Carbon monoxide (CO) emissions shall not exceed 83.5 pounds per hour.

D.8.  Volatile organic compound.  Volatile organic compound (VOC) emissions shall not exceed 10.9 pounds per hour.

Test Methods and Procedures

D.9.  Emissions Tests.  See common condition number O.1.

D.10.  Visible Emissions.  EPA test method 9

| EU | Unit | Result | Date |
| --- | --- | --- | --- |
| 036 | Cogen | Passed | 12/18/2002 |

D.11.  Nitrogen Oxides EPA test method 20.  Testing is required only upon permit renewal.

D.12.  Carbon monoxide.  EPA test method 10.  Testing is required only upon permit renewal.

D.13.  Volatile organic compound.  EPA test method 25A.  Testing is required only upon permit renewal.

D.14.  Determination of Process Variables.  See common condition number O.2.

### Accuracy is assured through periodic calibrations and PM.

Periodic Monitoring

D.15.  Natural Gas Usage.   Natural gas usage heat input will be calculated on an hourly basis and recorded in units of MMBtu/hr.

Records:  Y-T-D records show this condition is met.

D.16.  Steam/Fuel Ratio.   Monitor and record the steam to fuel ratio on an hourly basis.

### Records:  The steam to fuel ratio is monitored on an hourly basis.  The ratio is fuel flow in pounds per second to steam flow in pounds per second.  The ratio generally runs from 0.5 to 1.5 based on the load.

AREA V—MALEIC ANHYDRIDE PLANT

Solutia Representative:  Michael Greene

Subsection C.  This section addresses the following emissions units.

| E.U. ID No. | Brief Description |
| --- | --- |
| 076 | Maleic Anhydride (MA) Plant |

Operation of a maleic anhydride plant with a design capacity of 260 million pounds per year of maleic anhydride.  The reaction is carried out in four reactors using butane as a raw material with off gases separated in two product recovery units and combusted in Boilers 7 and 8.

Approximately 6.5 million standard cubic feet per hour of off gas is emitted from each pair of reactors, which contains approximately 9,000 pounds per hour of carbon monoxide (CO) and 7,000 pounds per hour of volatile organic compounds (VOC) at design rates.  The balance of the off gas stream is H20, C02, N2 and 02.  Emissions of CO and VOC are controlled by burning in Boilers 7 and 8.  The two off gas headers are cross-connected, but normal flow is from reactors 1 and 2 to boiler 7 and from reactors 3 and 4 to Boiler 8.

During startup, shutdown or malfunction of the maleic anhydride plant, waste gases are vented without control.  This is required for safety.  Such venting is conditionally allowed.

This emissions unit is regulated under applicable portions of NSPS – 40 CFR 60 Subparts A, Kb, VV, and III; NESHAPs – 40 CFR 63 Subparts A, F, G and H, adopted and incorporated by reference in Rule 62-204.800, F.A.C.

Essential Potential to Emit (PTE) Parameters

C.1.  Capacity. The maximum gas flow rate from the maleic anhydride to each boiler shall not exceed 6.5 MMscf/hour (13.0 MMscf/hour total to both boilers). {Regular record keeping is not required for capacity limitations.}

Y-T-D records indicated a rate of <6.5 MMscf/hr.  The rate is monitored online to ensure that remains below the capacity limit.

C.2.  Hours of Operation.  This emissions unit is allowed to operate continuously, i.e., 8,760 hours/year.

Emission Limitations and Standards

C.3.  During startup, shutdown, and control system malfunctions this source shall not exceed emissions resulting from a production rate of 130 MM pounds MA per year and shall comply with the following emission limits.

Emission limits and formulas: (Administrative correction 2/18/03)

- Emissions shall not exceed 1,750 pounds of either VOC (calculated as butane) or CO per reactor hour for startups and malfunctions; or 875 pounds of either VOC or CO per reactor hour for shutdowns;

- No more than one and one-half reactor hours shall be used for an individual reactor startup or shutdown;

- No more than eight reactor hours shall be used for a total production startup; and

- No more than six hours shall be used during a control system malfunction to allow sufficient time to trouble shoot and correct the problem.

These limits and formulas are reflected in the following table:

| Number |  | Startup |  |  | Shutdown |  |  | Malfunction |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Of | Maximum | Pounds |  | Maximum | Pounds |  | Maximum | Pounds |  |
| Reactors | Vent Hrs. | CO | VOC | Vent Hrs. | CO | VOC | Vent Hrs. | CO | VOC |
| 1 | 1.5 | 2,625 | 2,625 | 1.5 | 1,313 | 1,313 | 6 | 10,500 | 10,500 |
| 1 | 1.5 | 5,250 | 5,250 | (Second reactor on line, separate startup) |
| 2 | 4 | 7,000 | 7,000 | 4 | 3,500 | 3,500 | 6 | 21,000 | 21,000 |
| 3 | 6 | 10,500 | 10,500 | 6 | 5,250 | 5,250 | 6 | 31,500 | 31,500 |
| 4 | 8 | 14,000 | 14,000 | 8 | 7,000 | 7,000 | 6 | 42,000 | 42,000 |

During boiler malfunctions the production rate of the reactors involved are operated at a reduced rate so as not to exceed the 10,500 pounds of CO and VOC allowed during a 6-hour malfunction period.  If the limit is approached, the reactor is shutdown.  The facility has determined that a feed rate not to exceed 160 kpph of air and 1.5% mole wt of butane will keep the CO and VOC emissions below the limit for a 6-hr period.

C.4.  Determination of Process Variables.  See common condition number O.2.

#### Periodic Monitoring

C.5.  Startup, Shutdown and Malfunction Log.  A log shall be maintained of all uncontrolled VOC and CO emissions resulting from startup, shutdown, and malfunctions.

Records Review:  Y-T-D records indicate compliance.  Records are maintained in a database and are very descriptive.

C.6.  Process Off-gas Rate.  Monitor and record process off-gas flows to boilers 7 & 8 on an hourly basis (MMSCF/hr).

Records Review: Y-T-D records indicated compliance with this condition.

AREA II--ADIPIC ACID

Solutia Representative: Randy Sheffield

Subsection E.  This section addresses the following emissions units.

| E.U. ID No. | Brief Description |
| --- | --- |
| 060 | Adipic Acid 485 BEPEX Dryer |
| 061 | Adipic Acid Dryer 405-A |
| 062 | Adipic Acid Dryer 405-B |
| 063 | Adipic Acid Dryer 465-A |
| 064 | Adipic Acid Dryer 465-B |
| 079 | Adipic Acid 485 NIRO Dryer |

The following specific conditions apply to the emissions unit(s) listed above:

Essential Potential to Emit (PTE) Parameters

E.1.   Capacity. The maximum operating rate of these emission units is as follows:

| Dryer | EU-061 405A | EU-062 405B | EU-063 465A | EU-064 465B | EU-060 Bepex | EU-079 Niro |
| --- | --- | --- | --- | --- | --- | --- |
| Exhaust air blower horsepower, (HP) | 50 | 50 | 75 | 75 | 50 | 100 |
| Exhaust air blower, design maximum flow rate, (SCFM, hourly average basis, as determined by EPA method 2 stack test) | 8000 | 8000 | 10500 | 10500 | 10,200 | 10,500 |
| Dryer exhaust scrubber, water minimum circulation flow rate (PPH, hourly average basis) | 3000 | 3000 | 3000 | 3000 | 5500 | NA |
| Exhaust air, bag filter model number | NA | NA | NA | NA | NA | 2600+ sq. ft. filter area |
| Discharge air, design basis particulate concentration (grains/SCF, hourly average basis) | 0.10 | 0.10 | 0.10 | 0.10 | 0.015 | 0.015 |

NA = not applicable

Each dryer has an interlock system installed that will halt product feed if the flow rate drops below the required value or in the case of the Niro dryer the dp at the inlet and exit exhaust of the baghouse exceeds set limits.

E.2.  Common Conditions.

Emission Limitations and Standards

E.2.a.  Visible Emissions.  The emissions units listed above shall not exceed 5 percent opacity.

Opacity at inspection: 0%

E.2.b.  Hours of Operation.  The emissions units listed above are allowed to operate continuously, i.e., 8,760 hours/year.

Test Methods and Procedures

E.2.c.  Emissions Tests.  See common condition number O.1.

E.2.d.  Visible Emissions.  EPA test method 9.  The capacity for VE tests is normal operations.

| EU | Unit | Result | Date |
| --- | --- | --- | --- |
| 060 | 485 BEPEX Dryer | Passed | 6/24/03 |
| 061 | Dryer 405-A | Passed | 6/10/03 |
| 062 | Dryer 405-B | Passed | 7/16/03 |
| 063 | Dryer 465-A | Passed | 5/13/03 |
| 064 | Dryer 465-B | Passed See E.2.f. | 6/9/03 |
| 079 | 485 NIRO Dryer | Passed | 6/24/03 |

E.2.e.  Particulate Matter.  EPA test method 5.  Testing is required only upon permit renewal.

E.2.f.  Compliance with the mass emission standard may be assumed, and a waiver of the PM testing requirements may be granted, if visible emissions are not greater than 5 percent opacity. If the results of the visible emissions tests show greater than 5 percent opacity, the permittee shall conduct a particulates test within 30 days to show compliance with the mass emission standard of the Department.

VE exceeded 5% on 5/13/03; PM test required in 30 days: Passed VE and PM test 6/9/03.

E.2.g.  Determination of Process Variables.  See common condition number O.2.

Accuracy is assured through quarterly calibration by the instrument shop.

Periodic Monitoring

E.8.  Reasonable Assurances.  The following work practices shall be followed to insure reasonable control of particulate matter:

(1)  Scrubbers or bag filters, associated with solids handling, are to be in service prior to commencement of activities such as loading, unloading, storing, handling or other industrially related activities. Shift operators keep a written log.

(2) Operation logs shall include documentation that particulate matter control devices (hoods, fans, filters or similar equipment) are activated before initiation of solid material handling activities.  This documentation will be maintained and made available for Department inspections.  Such information is maintained.

(3) Visible emissions testing shall be conducted on an annual basis to provide reasonable assurance of system effectiveness.  To perform the visible emissions testing, it will be necessary to have material handling ongoing at reasonable or typical activity levels.  No operating rate limits will apply to this testing, however Solutia commits to ensure that operating rates are representative of normal operating conditions.  A log of operating rates shall be maintained on a daily basis.  The operating rates during testing shall be noted on the test report.  These operating rate logs and visible emissions tests will also be maintained and will be made available for Department inspection.

Review of records and procedures:  Y-T-D records review indicates compliance with the above requirements.

E.9.  Blower Capacity.  Maintain records of blower capacity, motor size and model number for each dryer.  Blower capacity will be confirmed with a pitot tube during required PM testing.

Records review:  The required information is maintained.

E.10.  Scrubber Water Flow.  Maintain hourly average scrubber water flow rate for EUs 060-064.

Y-T-D records reviewed.  In all instances where the flow dropped below the required value, the interlock safeguard stopped the product feed.

This section addresses the following emissions unit(s).

| E.U. ID No. | Brief Description |
| --- | --- |
| 002 | Area II Adipic Acid Expansion - TRU/SCR1; existing TRU and new SCR (or equivalent) - SCR2; Backup new SCR (or equivalent) - Process Equipment; Product Synthesis, Refining and Raw Material Recovery |

A ketone and alcohol mixture (KA, cyclohexanone/cyclohexanol) is oxidized with nitric acid to produce an Adipic Acid solution.  The solution is refined by chilling due to vacuum evaporation, forming Adipic Acid crystals at the bottom of the process vessel.  The resulting slurry is centrifuged to remove water and form a wet cake.  The wet cake is redissolved in pure water and the purified Adipic Acid solution is sent to the Nylon Salt Strike or Drying and Product Loading operations.  Emissions of CO and VOCs and NOx will be controlled by sending them to the TRU/SCR1 or the SCR2.  This emission unit has a construction permit (0330040-011-AC; 1100 MAR) to expand production.  Upon completion of the construction project the NOx limitation will be 150 ppm.

Status: The Area II Adipic Acid Expansion to 1100 MAR was permitted originally under 0330040-011-AC.  The conditions in Subsection F below were taken from that construction permit and used in the Title V permit.  Because much of the equipment, operations and procedures were unknown at that time, only general references were made to the NSPS and NESHAP requirements.  Since the 1100 MAR permit has not been entered,  many of the requirements are not yet determined and not all of the conditions are in effect for the 1100 MAR project.

The facility is currently operating under the 850 MAR requirements.  The requirements for this rate are being met.  All the permit conditions are included for information.

The following specific conditions apply to the emissions unit(s) listed above:

Essential Potential to Emit (PTE) Parameters

F.1.a.  Capacity. The maximum allowable operating rates for each, the TRU/SCR1, and the SCR2, shall not exceed the rate of all combined process gases from the Area 471 gas phase hydroxylation reaction and product refining and raw material recovery processes, the Area I HALCON stream, and the Area II process gases, generated at the Area 471 maximum operating rate of 55,000 lbs Phenol/hr (hourly average basis), the Area I maximum operating rate of 82,000 lbs process air/hr (hourly average basis), and the Area II maximum operating rate of 119,059 lbs KA feed/hr (hourly average basis).  {Regular record keeping is not required for capacity limitations.}

F.1.b.  Capacity.  The process/operation rate for the Area II Process Equipment; Product Synthesis, Refining and Raw Material Recovery, shall not exceed the maximum operating rate of 119,059 lbs KA feed/hr (hourly average basis), up to 1,100 Million Pounds Adipic Acid produced per 12 months (1,100 MAR) on a 12 month rolling total basis.  Permittee shall maintain records of KA feed on an hourly basis, monthly totals, and 30 day and 12 month rolling averages.  Permittee shall also maintain records of adipic acid production on a daily basis, monthly totals and 12 month rolling totals.  These records shall be made available for Department inspection.

The 850 MAR limit is 92,000 lb KA feed per hour.

Review Records: Hourly, monthly and 30 day	 and 12 month rolling totals are maintained.  As of Aug 30, 2003, the MAR was 682 tons.  The highest rate noted during the Y-T-D records review was 708 tons.  The highest KA feed was 88,000 pph.

F.2.a.  Methods of Operation - Gases Processed.  The Area II TRU/SCR shall be used to control CO, VOC and NOx emissions from Area 471 processes and support activities, the Area I HALCON process offgas stream, and the emissions from Area II.

Status of SCR1:  Catalyst is not installed.  It is not needed to meet the 500 ppm required of 850 MAR.  There were problems with fouling and the cause has not been identified.

F.2.b.  Methods of Operation - Fuels.  The Area II TRU/SCR shall only use natural gas, ethane or butane as primary fuels.

Nothing else is used.

F.3.  Hours of Operation.  This emissions unit is allowed to operate continuously, i.e., 8,760 hours/year, as long as the annual production limit is observed.  A log of TRU/SCR1, SCR2, NOx Compressor 1 and Backup NOx Compressor 2 on-line time shall be maintained and made available for department inspection.  The log time-keeping requirement may be modified if, after compliance testing, it is shown that emissions from the TRU/SCR1 and the SCR2 are equivalent to obviate this requirement.

These logs were reviewed and contained the required information.

Emission Limitations and Standards

F.4.  The NOx emission concentration shall not exceed 150 ppm, on a rolling 24-hour average, from each of the TRU/SCR1 or the SCR2, and the annual total NOx emissions from both shall not exceed 236 tons/year on a rolling 12-month basis.  This shall be demonstrated by means of a NOx Continuous Emissions Monitor (CEM), which is operated under a Department approved QC plan, while firing the process gases from Area I, Area 471 and Area II.  This monitoring system shall be operational upon startup of the 1st phase of construction for reasonable assurance of estimates used in application.  {Permitting note: NOx emissions of a maximum of 500 ppm on a 30 day rolling average are allowed until construction (permit 0330040-011-AC) is complete.  Until construction is complete, the adipic acid production shall not exceed an annual capacity of 850 million lbs/year (850 MAR)}.

Review of records and status of construction:  The facility has not started construction on the expansion project.  It operating under the 850 MAR requirements.  A review of emission records indicates the 500 ppm limit is being met.  Y-T-D records indicated emissions of 450 ppm or less.

Reasonable Assurances

F.5.a. Upon completion of construction (permit 0330040-011-AC), the permittee shall demonstrate continuous compliance that the NOx emission shall not exceed 150 ppm, on a rolling 24-hour average and 236 tons/year, on a rolling 12-month basis, from the exhaust stacks of the TRU/SCR1 and the SCR2.  This shall be demonstrated by proper installation, maintenance and operation of Continuous Emission Monitors (CEMs) for NOx from the exhaust stacks of the TRU/SCR1 and SCR2, in conformance with a Department approved QC plan and annual CEMs RATA testing.  CEMs readings shall be continuously recorded, and rolling 24 hour, 30 day and 12 month calculated averages shall be recorded and made available for Department inspection.  Annual compliance testing may be waived if the Department receives reasonable assurance that the CEMs and data processing/recording systems have been functioning properly.   No construction.

F.5.b.  Permittee shall implement and maintain a Department-approved Quality Control (QC) program which, at a minimum, follows the quality assurance procedures set forth in 40 CFR Appendix F, Quality Assurance Procedures, and Appendix B, Performance Specifications 2 and 6, to ensure the proper operation of the CEMs used to measure NOx concentrations and the instrumentation used to measure process parameters used to calculate the NOx emissions from the exhaust stacks of the TRU/SCR1 and the SCR2.  Permittee shall submit a draft QC program for Department approval 180 days before startup of the first phase of the expansion.

Records review indicates the above conditions are being met for the installed NOx CEMS.

The following specific conditions apply to the NSPS emissions unit(s) listed above:

40 CFR 60 Requirements

F.6.  This emissions unit shall comply with all applicable requirements of 40 CFR 60 Subparts A, VV, NNN and RRR, incorporated by reference. TRE>1.

The reconstructed adipic acid production area “A” distillation column commenced initial start-up on December 9, 2000 (Solutia Ltr., 12/20/00). The project will ultimately support increased operating rate beyond 850 MAR.   Reconstruction of the “A” distillation column completed a phased upgrade of the double effect concentrating distillation train system.  This reconstruction put the A/C and D/B double effect distillation concentration system under 40 CFR 60 Subpart NNN.  To comply with  §60.662(c), Solutia elected to maintain a TRE Index value greater than 1.0 without use of VOC emission control devices (Solutia Ltrs, 12/20/00 and 12/14/01).   Emissions testing to determine a TRE value was completed April 11, 2001.  The results for the compounds did not meet the EPA Method 18 criteria of 70-130% recovery of the spike compounds.  Because of this, the highest average of raw parts per million or corrected ppm concentration of each compound was used to calculate an estimated TRE index for each source.  Using the highest concentration of each compound will give the worst possible TRE index.  These TRE values showed indices above one (TRC Emissions Test Report, July 2001).  This project will ultimately support increased operations beyond the 850 MAR.  Once the problems with the test procedure are solved, the TRE indices will have to be reevaluated.  An workable absorbent compound has not been found.

The following specific conditions apply to the NESHAPs emissions unit(s) listed above:

40 CFR 61 Requirements

F.7.  This emissions unit shall comply with all applicable requirements of 40 CFR 61 Subparts A, and V, incorporated by reference.

NOTE:  This emissions unit is also subject to applicable conditions contained in the Common Conditions section of this subsection.

| E.U. ID No. | Brief Description |
| --- | --- |
| 090 | Area II Adipic Acid Expansion - Fugitive Emissions |

Expansion under 0330040-0110AC, 1100 MAR,  has not taken place.

The following specific conditions apply to the emissions unit(s) listed above:

40 CFR 60 Requirements

F.8.  This emissions unit shall comply with all applicable requirements of 40 CFR 60 Subparts A and VV, incorporated by reference.

40 CFR 61 Requirements

F.9.  This emissions unit shall comply with all applicable requirements of 40 CFR 61 Subparts A and V, incorporated by reference.

F.8 and 9.  There have been no production increases beyond 850 MAR.

NOTE:  This emissions unit is also subject to applicable conditions contained in the Common Conditions section of this subsection.

Common Conditions.

| E.U. ID No. | Brief Description |
| --- | --- |
| 002 | Area II Adipic Acid Expansion - TRU/SCR1; existing TRU and new SCR (or equivalent) - SCR2; Backup new SCR (or equivalent) - Process Equipment; Product Synthesis, Refining and Raw Material Recovery |
| 090 | Area II Adipic Acid Expansion - Fugitive Emissions |

Expansion under 0330040-0110AC, 1100 MAR,  has not taken place.

The following specific conditions apply to the emissions unit(s) listed above:

Test Methods and Procedures

F.10.a.  Emissions tests are required to show compliance with the standards of the Department.  The test results must provide reasonable assurance that the source is capable of compliance at the permitted maximum operating rate. The compliance test protocol shall be determined by the DEP Rule or the EPA Regulation applicable to the specific Emission Unit, upon verification and approval of the additional information required by specific condition F.17. following design finalization.  Such tests shall be scheduled within 90 days after initial operation.  The Department shall be notified at least 15 days prior to testing to allow witnessing.  Results shall be submitted to the Department within 45 days after testing.

F.10.b.  The test reports shall comply with applicable portions of Rule 62-297.310, F.A.C., Test Reports.  The Department can require special compliance tests in accordance with Rule 62-297.310(7) F.A.C.  Other test methods and alternate compliance procedures may be used only after prior Departmental approval has been obtained in writing.

F.10.c.  Testing of emissions shall be conducted with the source operating at capacity.  Capacity is defined as 90-100% of rated capacity.  If it is impractical to test at capacity, then sources may be tested at less than capacity; in this case, subsequent source operation is limited to 110% of the test load until a new test is conducted.  Once the unit is so limited, then operation at higher capacities is allowed for no more than 15 days for purposes of additional compliance testing to regain the rated capacity in the permit, with prior notification to the Department.

Reasonable Assurances

F.11.  Permittee shall submit specific information including new equipment description and rule applicability analysis for updating the permit file as required by specific conditions in the NSPS and NESHAPs Common Conditions of this subsection.  This information shall include applicable emissions standards, compliance testing, reporting, recording and monitoring requirements for each emission unit.  Permittee shall submit the required information for Department approval 180 days before startup of the 1st phase of expansion.  The approved listing of applicable emissions standards, compliance testing, reporting, recording and monitoring requirements for each emission unit shall be incorporated, and become a part of, this permit.

F.12.  All appropriate emissions control systems; The Area II TRU/SCR1, the Area II backup NOx compressor (2), the SCR2, and the CEMs and their data processing/recording systems shall be in place and operational before each of the Area II process construction phases may be started up.

The TRU/SCR1, NOx compressors, SCR2 and CEMs are in place.  The SCR1 is not operational due to catalyst fouling.  It is not needed to maintain NOx emissions at the 500 ppm level for the 850 MAR.

F.13.a.  Permittee shall conduct a testing program to re-evaluate the sources and amounts of HCN emitted by the Area II process TRU vent stream, upon completion of each of the major phases of construction.

F.13.b.  Permittee shall conduct a testing program to determine baseline emissions before construction, and emissions changes of NOx, VOC, PM and CO emitted by the Area II process TRU vent stream, upon completion of each of the major phases of construction.

NSPS Common Conditions.

| E.U. ID No. | Brief Description |
| --- | --- |
| 002 | Area II Adipic Acid Expansion - TRU/SCR1; existing TRU and new SCR (or equivalent) - SCR2; Backup new SCR (or equivalent) - Process Equipment; Product Synthesis, Refining and Raw Material Recovery |
| 090 | Area II Adipic Acid Expansion - Fugitive Emissions |

Expansion under 0330040-0110AC, 1100 MAR,  has not taken place.

The following specific conditions apply to the NSPS emissions unit(s) listed above:

40 CFR 60, - Requirements

F.14.  These emissions units shall comply with applicable conditions of 40 CFR 60 Subparts A, Kb VV, NNN and RRR, incorporated by reference.

F.15.  Permittee shall submit, for Department approval, at least 180 days prior to startup, the following information to determine final applicability and standards for each emission unit:

40 CFR 60 Sp Kb

F.15.a.  list of all new or modified Volatile Organic Liquid Vessels, including description of construction and emission control device(s), location, service, size, and  characteristics of liquid stored (ref. to 40 CFR 60 Sp Kb, 60.116b), with a written determination of:  40 CFR 60 Sp Kb, 60.110b emission control device(s), 40 CFR 60 Sp Kb, 60.112b, testing and procedures requirements of  40 CFR 60 Sp Kb, 60.113b, and the reporting and recordkeeping requirements of 40 CFR 60 Sp Kb, 60.115b, as applicable to this emission unit and its segments.

40 CFR 60 Sp VV

F.15.b.  list of all new or modified equipment (defined in ss 60.481) affected under 40 CFR 60 Sp VV, 60.480 affected equipment location, service, size, and characteristics of material(s) handled (ref. to 40 CFR 60 Sp VV, 60.481), with a written determination of: standards requirements of 40 CFR 60 Sp VV, 60.482-(1_10), test methods and procedures of 40 CFR 60 Sp VV, 60.485 and the reporting and recordkeeping requirements of 40 CFR 60 Sp VV, 60.487, as applicable to this emission unit and its segments.

40 CFR 60 Sp NNN

F.15.c. list of all new or modified distillation equipment (defined in ss 60.661) affected under 40 CFR 60 Sp NNN, 60.660, affected equipment location, service, size, and characteristics of material(s) handled (ref. to 40 CFR 60 Sp VV, 60.661), with a written determination of the standards requirements of  40 CFR 60 Sp NNN, 60.662, monitoring of emissions and operations of 40 CFR 60 Sp NNN, 60.663 test methods and procedures of 40 CFR 60 Sp NNN, 60.664 and the reporting and recordkeeping requirements of 40 CFR 60 Sp NNN, 60.665, as applicable to this emission unit and its segments.

40 CFR 60 Sp RRR

F.15.d. list of all new or modified reactor process equipment (defined in ss 60.701) affected under 40 CFR 60 Sp RRR, 60.700, affected equipment location, service, size, and characteristics of material(s) handled (ref. to 40 CFR 60 Sp RRR, 60.701), with a written determination of: the standards requirements of  40 CFR 60 Sp RRR, 60.702, monitoring of emissions and operations of 40 CFR 60 Sp RRR, 60.703, test methods and procedures of 40 CFR 60 Sp RRR, 60.704 and the reporting and recordkeeping requirements of 40 CFR 60 Sp RRR, 60.705, as applicable to this emission unit and its segments.

NESHAPs Common Conditions.

| E.U. ID No. | Brief Description |
| --- | --- |
| 002 | Area II Adipic Acid Expansion - TRU/SCR1; existing TRU and new SCR (or equivalent) - SCR2; Backup new SCR (or equivalent) - Process Equipment; Product Synthesis, Refining and Raw Material Recovery |
| 090 | Area II Adipic Acid Expansion - Fugitive Emissions |

Expansion under 0330040-0110AC, 1100 MAR,  has not taken place.

The following specific conditions apply to the NESHAPs emissions units listed above:

40 CFR 61, - Requirements

F.16.  These emissions units shall comply with applicable conditions of 40 CFR 61 Subparts A and V, incorporated by reference.

F.17.  Permittee shall submit, for Department approval, at least 180 days prior to startup, the following information to determine final applicability and standards for each emission unit:

40 CFR 61 Sp V

F.17.a. list of all new or modified equipment (defined in ss 61.241) affected under 40 CFR 61 Sp V, 61.240 affected equipment location, service, size, and characteristics of material(s) handled (ref. to 40 CFR 61 Sp V, 61.241) with a written determination of: the standards requirements of  40 CFR 61 Sp V, 61.242-(1_11), test methods and procedures of 40 CFR 61 Sp V, 61.245, recordkeeping requirements of  40 CFR 61 Sp V, 61.246, and the reporting requirements of  40 CFR 61 Sp V, 61.247, as applicable to this emission unit and its segments.

YARN UTILITIES & NYLON POLYMERIZATION PLANT

Solutia Representatives:  Bill Weeks, Teresa Knepper and Billy Rogers

Subsection G.  This section addresses the following emissions units.

| E.U. ID No. | Brief Description |
| --- | --- |
| 005 | Vaporizer No.1 |
| 007 | Vaporizer No.2 |
| 008 | Vaporizer No.3 |
| 009 | Vaporizer No.4 |
| 010 | Vaporizer No.5 |
| 011 | Vaporizer No.6 |
| 013 | Vaporizer No.7 |
| 075 | Vaporizer No.8 |

Operation of eight vaporizers.  Total capacity is 136 million Btu/hour heat input total for all vaporizers.  There are no individual vaporizer limits beyond this total limit.  These emissions units are primarily fueled by natural gas.  No. 2 fuel oil with a maximum of 0.5 % sulfur by weight is allowed as an emergency fuel.  Vaporizer No. 8 is regulated under applicable portions of NSPS - 40 CFR 60 Subparts A and Dc., adopted and incorporated by reference in Rule 62-204.800, F.A.C.

Records Y-T-D show heat input well below 136 MMBtu/hr.

Energy conservation features, which do not effect emissions, have been incorporated into the Vaporizer facility.  Vaporizer unit exhausts have been consolidated in some cases.  The facility is still capable of exhausting through individual stacks, if necessary.  The discharge arrangement is given below:

Source I.D. Number	Vaporizer Unit		Stack Number

EU-005			Vaporizer No.1		Stack No.4

EU-007			Vaporizer No.2		Stack No.2

EU-008			Vaporizer No.3		Stack No.5

EU-009			Vaporizer No.4		Stack No.4

EU-010			Vaporizer No.5		Stack No.5

EU-011			Vaporizer No.6		Stack No.6

EU-013			Vaporizer No.7		Stack No.6

EU-075			Vaporizer No.8		Stack No.8

The following specific conditions apply to the emissions unit(s) listed above:

Essential Potential to Emit (PTE) Parameters

G.1.  Methods of Operation- Fuels.  The primary fuel shall be natural gas.  No. 2 fuel oil with a maximum of 0.5% sulfur by weight may be use as an emergency fuel only.  The permittee shall immediately notify the Department of each emergency use of No. 2 fuel oil and if such use exceeds four days a visible emissions compliance test shall be conducted on each unit burning fuel oil.  No. 2 fuel oil burned during routine interlock Preventive Maintenance is exempt from this notification requirement.

Interlock Preventive Maintenance no longer used. No fuel oil used in several years.  Enough stored to run about an hour.

G.2.  Hours of Operation.  This emissions unit is allowed to operate continuously, i.e., 8,760 hours/year.

Emission Limitations and Standards

G.3.  Visible Emissions.  Visible emissions shall not exceed 10% opacity under normal operating conditions.

Inspection: none observed.

Test Methods and Procedures

G.4.  Emissions Tests.  See common condition number O.1.

G.5.  Visible Emissions.  EPA test method 9.  Visible emissions testing is only required when burning No 2 fuel oil or upon Department request.

NA: Fuel oil not used.

G.6.  Special Compliance Tests.  If Department inspections observe visible emissions above 5% opacity on any vaporizer and/or stack, it shall be considered reason to believe the visible emissions standard could be violated; therefore, a special visible emissions compliance test shall be conducted to show compliance with the emission standard.

G.7.  Determination of Process Variables.  See common condition number O.2.

Accuracy assured through annual calibration.

Periodic Monitoring

G.7.  Natural Gas Usage.  An aggregate natural gas usage heat input will be calculated on an hourly basis and recorded in units of MMBtu/hr for vaporizers 1 through 8 combined.

Y-T-D Records: Condition met.

Subsection H.  This section addresses the following emissions unit(s).

| E.U. ID No. | Brief Description |
| --- | --- |
| 081 | Continuous Nylon Polymerization LinesContinuous and Batch Polymerization Processes Modifications |
| 082 | Batch Nylon Polymerization |

Nylon salts are mixed, concentrated and polymerized to form a molten polymer by both continuous and batch processes.  The molten polymer is solidified to nylon fiber from the continuous lines and flake products from the batch lines.  Unconfined emissions of organic compounds occur during this solidification and are vented away from the working areas and discharged without controls.

The twelve continuous polymerization lines normally operate using an Evaporator/Reactor/Finisher process design or an alternative polymerization method, involving an Evaporator/Pre-reactor/

Reactor/Finisher process design.  Each continuous line has a separate evaporator.  A portion of evaporator emissions is used to preheat the nylon salts, and the remaining emissions are normally fed to a distillation column shared by other yarn plant equipment.  Pre-reactor steam and emissions are also fed to the distillation column control device.  Reactor steam is condensed to produce process steam and the condensate is handled as wastewater.  The emissions from the Finishing step are controlled by monomer scrubbers.

Four batch evaporators cyclically feed the batch lines’ twelve autoclaves where the batch polymerization takes place.  The autoclave emissions are also normally fed to the distillation column.  The organics recovered by the distillation column are used as supplemental fuel in power boilers or routed to the plant process waste disposal system.

Essential Potential to Emit (PTE) Parameters

H.1.  Hours of Operation.  This emissions unit is allowed to operate continuously, i.e., 8,760 hours/year.

Emission Limitations and Standards

H.2.  The maximum allowable emissions rate for VOCs is 715 lbs/day as a rolling annual average.

Jan-Jun, 2003 rolling totals were 278 lbs/day average or less.

#### Test Methods and Procedures

H.3.  Emissions Tests.  See common condition number O.1.

H.4.  VOC emissions testing shall be conducted every two years using the Yarn Plant Emissions Sampling Protocol, dated June 3, 1993.

Test sampling completed 9/4/03.  As of the inspection date the test results had not been received.

H.5.  Emission factors shall be revalidated every two years.  The results shall be submitted no later than 45 days after completion of testing.

To be submitted with test report.

H.6.  Determination of Process Variables.  See common condition number O.2.

Accuracy assured through annual calibration.

Periodic Monitoring

H.7.  The permittee shall maintain a log of down time for each control device, which controls emissions of organic compounds.

Review Log: Hand written log maintained.

H.8.  The permittee shall calculate at a minimum once annually or as requested by the Department a  "365 day moving average" of total organic emissions from EU-081 and EU-082 using current emissions factors.  A summary graph identifying each day's average shall be attached to and submitted with each annual operating report.

Jan-Jun, 2003 records rolling total 278 pounds or less.  Graph submitted.

H.9.  Distillation Column.  The permittee shall monitor the operation and performance of the distillation column.  As a minimum, the monitoring shall include the following:

a) monthly monitoring of off gas HMDA concentrations.

b) monitoring and maintaining a minimum acceptable column reflux flow of 5000 lbs/hr

hourly average.

c) records shall be maintained and made available for Department inspection.

- Sampled weekly.

- Y -T-D records review.  Generally 8-9 kpph.

- On hand.

### AREA I—CYCLOHEXANE OXIDATION, NITRIC ACID & AREA 480 KA

Solutia Representatives:  Carla Crystal and Michelle Schotts

Subsection I.  This section addresses the following emissions unit(s).

| E.U. ID No. | Brief Description |
| --- | --- |
| 020 | Cyclohexane Oxidation Process |

Cyclohexane is oxidized with air in two high-pressure reactor trains.  Two high-pressure scrubbers reduce the loss of volatile organic compounds (VOC).  Emissions are primarily VOC and carbon monoxide (CO).  Further VOC and CO emissions reductions are effected by routing the emissions from the high-pressure scrubbers to a NOx thermal reduction unit when operating.  The reactors are discharged to cyclohexane recovery, product refining, and distillation operations.  Emissions from these operations are controlled by two low-pressure scrubbers, which vent to atmosphere.  The emissions from low-pressure scrubbers are of similar composition but lesser quantity than those from high-pressure scrubbers.  Total process emissions of volatile organic compounds are estimated at 926 pounds per hour and emissions of carbon monoxide are estimated at 1,404 pounds per hour and are only determined during required emissions testing.

The Cyclohexane Oxidation Process has a cyclohexanone/cyclohexanol (KA) Recovery Column which functions as a separator for product KA, water and impurities.  The overhead vapors pass through an overhead condenser into a decanter where the aqueous and hydrocarbon streams are separated.  The aqueous phase is further processed for recovery.  The hydrocarbon stream is routed to product streams for refining.  The vapors from condenser and decanter are mixed with other streams to feed one of the low-pressure scrubbers.  The condenser system operates with the sump temperature below 50(C.  The condenser sump temperature is monitored and recorded.

This emissions unit is regulated under applicable portions of NSPS - 40 CFR 60 Subparts A and NNN; NESHAPs - 40 CFR 61 Subpart FF, adopted and incorporated by reference in Rule 62-204.800, F.A.C.

The following specific conditions apply to the emissions unit(s) listed above:

Essential Potential to Emit (PTE) Parameters

I.1.  Capacity. The maximum allowable operating rate for the Cyclohexane Oxidation Process is 82,000 pounds per hour process air.

Inspection Rate: Y-T-D records review incompliance.  High 80,000 pph.

I.2.  Methods of Operation.  Oil flow through each of the high-pressure scrubbers shall be maintained at or above 3600 pounds per hour during reactor train operation. Flow rate indicator values shall be monitored and averaged values logged at no larger than one-hour intervals.  Records shall be maintained and made available for Department inspection.  Further VOC and CO emissions reductions will be made by routing the emissions from the scrubbers to the NOx Thermal Reduction Unit.  The KA recovery column shall vent to the condenser and from there to the low-pressure scrubbers.  The KA recovery column/condenser shall maintain a total resource effectiveness value greater than 1 .0, as applicable under NSPS 40 CFR Part 60 Subpart NNN.

Records Review:  Y-T-D records reviewed indicated compliance.  Generally, average 19-21 kpph.

I.3.  Hours of Operation.  This emissions unit is allowed to operate continuously, i.e., 8,760 hours/year.

Emission Limitations and Standards

I.4.  Emissions Tests.   See common condition number O.1.

I.5.  Carbon monoxide and volatile organic compounds.  Carbon monoxide and volatile organic compounds emissions tests shall be conducted in accordance with the approved alternative testing plan dated October 25, 1994.  Testing is required only upon permit renewal.

I.6. Subpart NNN.  For the KA Recovery Column, the owner or operator shall comply with the testing method, recordkeeping, and reporting requirements under NSPS, 40 CFR 60, Subpart NNN, Standards of Performance of VOC emissions from SOCMI Distillation Processes.

[Rule 62-296.800 and 62-204.800(7)63. F.A.C. and permit AC17-247476]

Monitoring of Operations

I.7.  For the KA Recovery Column applicable monitoring and recording devices shall be operated and maintained as per NSPS 40 CFR Part 60 Subpart NNN Regulations to monitor the operation of the condenser.

Recordkeeping and Reporting Requirements

I.8.  For the KA Recovery Column applicable reporting and record keeping requirements of NSPS 40 CFR Part 60 Subpart NNN Regulations shall be adhered to. Records shall be maintained and kept available for inspection by the Department.

Records Review: On hand.

I.9.  Determination of Process Variables.  See common condition number O.2.

Accuracy assured through calibrations on annual PM schedule.

Periodic Monitoring

I.10.  Process Air Rate.  Monitor and record total process air rate on an hourly basis (lbs/hr air).

### Records Review: Y-T-D records indicate compliance.

I.11.  High-Pressure Scrubber Oil Flow Rate.  Monitor and record high-pressure scrubber oil flow rate on an hourly basis (lbs/hr oil).

Records Review: Y-T-D incompliance.

I.12.  KA Recovery Column Condenser Sump Temperature.  Monitor and record hourly average sump temperature on an hourly basis (aver(C/hr). (50 deg C max)

Records Review: Y-T-D records indicated temperatures well within range.

Subsection L.  This section addresses the following emissions unit(s).

| E.U. ID No. | Brief Description |
| --- | --- |
| 042 | Nitric Acid Plant Continuous and Batch Polymerization Processes Modifications |

Operation of a nitric acid plant with a maximum capacity of 1500 tons per day.  NOx emissions are controlled by process operating conditions and/or use of a Selective Catalytic Reduction (SCR) NOx abatement device.

In the synthesis process, ammonia is oxidized in the presence of a catalyst to form NOx, which is then converted to HNO3 by a reaction with water.  Startup shutdown malfunction allowance is

3 hrs based on NSPS Subpart G rule.

This emissions unit is regulated under applicable portions of NSPS - 40 CFR 60 Subparts A, G, and Appendix F adopted and incorporated by reference in Rule 62-204.800, F.A.C.

Essential Potential to Emit (PTE) Parameters

L.1.  Capacity.  The maximum allowable operating rate is 1500 tons of 100% nitric acid produced per day.  { Regular record keeping is not required for capacity limitations.}

Currently limited to 1294 tons per day based on 2003 test rate.  Records Y-T-D indicate

L.2.  Hours of Operation.  This emissions unit is allowed to operate continuously, i.e., 8,760 hours/year.

Monitoring of Operations

L.3.  When the SCR Unit is not employed, the absorber column chilled water shall be monitored and water flow shall be maintained between 200 gal/min and 440 gal/min, and water temperature shall be maintained between 32(F and 54(F.

*COMPLIANCE ISSUE.   Based on a Y-T-D records review, the water flow and temperature were within the required limits except two instances when the water flow went above 440 gpm.  The first instance was April 14 for 10 minutes and the second was June 3 for 15 minutes.  Solutia discovered the excursion during a self-audit and reported it on 8/15/03 and it was reported in the Semiannual Monitoring Report.  Standard practice instructions were changed to require the operator to ensure the flow rate is in the proper range before taking the SCR offline.  The 440 cap may be meaningless since the greater the water flow, the better emissions are controlled.  The Department is looking into the validity of the upper limit of 440 gpm.

L.4.  Records of daily production, hours of operation, absorber column operating parameters and continuous emission monitor maintenance (down time, calibrations, and adjustments) shall be maintained and be available for inspection by the Department.

Records Review:  Proper records are maintained.

L.5.  The zero and span drift of the continuous emission monitor for NOx shall be checked at least once daily, and adjustments shall be made to zero and span whenever they exceed 2% and 2.5%, respectively.  This shall be done consistent with 40 CFR 60.13(d).

Records review:  Records Y-T-D indicated daily checks are made and adjustments are promptly made as required.

L.6.  The Permittee shall routinely monitor performance of the SCR Unit to ensure compliance with the emission limit. The monitoring information shall include the following:

L.6.a. Monitoring, logging and record keeping of

- SCR Inlet flow

- Ammonia flow to SCR (or ammonia valve position)

- Air flow to SCR

Records Review: These records are maintained.  These are indicators of when the SCR is on or off line.

L.7.  A conversion factor is established in accordance with 40 CFR 60.73 (lbs NOx/ton nitric acid per ppm).  The conversion factor shall be reevaluated during each reference method performance test, and a written report included in the reference method test report.

### Conversion factor: 0.013 Lb NOx/ton NHO3/ppm NOx based on test done 6/11/2003.

Emission Limitations and Standards

L.8.  Visible Emissions.  Visible emissions shall be less than 10% opacity.

Inspection VE: 0% opacity at inspection.

L.9.  The maximum allowable annual emission rate for NOx is 3.00 lb/Ton of 100% HNO3.  The maximum allowable annual NOx emissions are 360 tons of NOx per year based on a 365 day rolling total amount as determined by the CEMs data and stack flow rate.

6/11/2003 emissions test rate:  1.80 lb NOx/ton NHO3 .  Y-T-D records indicate rolling 12-month totals are generally 280-300 tpd.   As of June 15, the 12-month total was 296.919 tpd.

Test Methods and Procedures

L.10.  Emissions Tests.  See common condition number O.1.

L.11.  Visible Emissions.  The test method for visible emissions shall be EPA test method 9, incorporated and adopted by reference in Chapter 62-297, F.A.C.

6/11/2003:  VE 0%.

L.12.  Nitrogen Oxides.  The test method for nitrogen oxides shall be EPA test method 7, 7A, 7B, 7C or 7D, incorporated and adopted by reference in Chapter 62-297, F.A.C.

Method 7A used during 6 Jun 03 testing.

L.13.  Determination of Process Variables.  See common condition number O.2.

Accuracy is assured through calibration of instrumentation.

#### Periodic Monitoring

L.14.  Continuous Emissions Monitoring.  Permittee shall operate and maintain a nitrogen oxides (NOx) continuous emissions monitor (CEM) on the exhaust stack for measurement of NOx concentration.  The pollutant gas mixtures under Performance Specification 2 and for calibration checks under 40 CFR 60.13(d) shall be nitrogen dioxide (NO2). The span value shall be 500 ppm of NO2.  Records shall be kept for a 365 day rolling total amount calculated in tons of NOx/yr.

Span:   Operated and maintained.   Records review:  Quarterly CGA done on 1/9/2003 and 5/30/2003.  RATA was done 6/12/2003.

AREA 480, KEATONE ALCOHOL PROCESS

Subsection M.  This section addresses the following emissions unit(s).

| E.U. ID No. | Brief Description |
| --- | --- |
| 088 | Area 480 KA Expansion – Product Synthesis, Refining and Raw Material Recovery and all related ancillary equipment and systems – VOC Control Flare or equivalent and a backup unit |

This process reacts phenol with hydrogen in a gas phase hydrogenation reaction for conversion to cyclohexanone/cyclohexanol mixture (KA).  The KA is used in dipic acid production.  Process emissions will be primarily VOC.  Fugitive emissions will be VOC; primarily cyclohexanone and cyclohexanol and VOC/HAP; primarily phenol.

The VOC emission control equipment for the Area 480 process will be a flare or equivalent and a backup unit, probably a flare.  This emission unit is part of a plant-wide expansion (construction permit 0330040-012-AC).

{Permitting note(s): (IMPORTANT REGULATORY CLASSIFICATIONS – the emissions unit is regulated under applicable portions of NSPS – 40 CFR 60, Subparts A, Kb, VV, NNN, and RRR; NESHAPs 40 CFR 61 Subparts A and V; NESHAPs 40 CFR 63 Subparts A, F, G, H, and VV)}

| E.U. ID No. | Brief Description |
| --- | --- |
| 089 | Area 480 KA Expansion – Fugitive Emissions |

{Permitting note(s): (IMPORTANT REGULATORY CLASSIFICATIONS – the emissions unit is regulated under applicable portions of NSPS – 40 CFR 60, Subparts A and VV; NESHAPs 40 CFR 61 Subparts A and V; NESHAPs 40 CFR 63 Subparts A, and H)}

Status of construction and operation:  Emission unit is in long-term shutdown.  Last product produced 5/20/01; idle status: all process fluids including HAPS removed from vessels and lines as of 7/19/02; flare shutdown 7/31/02.  Solutia continues to make the semiannual HON Subpart G periodic and startup, shutdown and malfunction reports.

AREA IV—HMD/DME/HYDROGEN PLANT

Solutia Representative:  Lakelyn McIntyre

Subsection J.  This section addresses the following emissions unit(s).

| E.U. ID No. | Brief Description |
| --- | --- |
| 049 | Hydrogen Generating Plant #1 |

Hydrogen is used in the production of hexamethylene diamine and other nylon intermediates chemicals.  A feedstock of natural gas or ethane-rich gas is desulfurized.  The gas is then heated in the reformer fueled by natural gas and waste process gas.  The combustion flue gases of the reformer are the only source of emissions.  Particulate emissions are controlled by proper combustion and nitrogen oxides are controlled by use of low NOx burners.

The following specific conditions apply to the emissions unit(s) listed above:

Essential Potential to Emit (PTE) Parameters

J.1.  Capacity.   The maximum allowable operating rate is 180 MMBtu per hour heat input.

Inspection rate:  108 MMBtu/ hr. Records Y-T-D records reviewed.  Rate < 180 MMBtu/hr.

J.2.  Methods of Operation - Fuels.  This emissions unit shall be fueled by natural gas and/or process waste gas.

J.3.  Hours of Operation.  This emissions unit is allowed to operate continuously, i.e., 8,760 hours/year.

Emission Limitations and Standards

J.4.  Visible Emissions.  Visible emissions shall be less than 20% opacity.

### Inspection VE: 0% opacity.

Test Methods and Procedures

J.5.  Emissions Tests.  See common condition number O.1.

J.6.  Visible Emissions.  EPA test method 9.  Aug 20, 2003 test passed.

J.7.  Determination of Process Variables.  See common condition number O.2.

Flow meters calibrated and adjusted as necessary during scheduled shutdowns.

Subsection K.  This section addresses the following emissions unit(s).

| E.U. ID No. | Brief Description |
| --- | --- |
| 040 | Hexamethylene Diamine Synthesis and Refining |
| 041 | B and C Hexamethylene Diamine Stripper Distillation Column |

Adiponitrile is hydrogenated to yield crude Hexamethylene Diamine (HMD).  The HMD is then refined by vacuum distillation.  A vacuum is achieved by staged steam jets.  The water soluble HMD is discharged in the steam condensate to the wastewater system.  The concentration of HMD in the noncondensible emissions is reduced in each stage.

The stripper distillation columns are subject to applicable requirements of 40 CFR Part 60, Subparts A and NNN, adopted and incorporated by reference in Rule 62-204.800, F.A.C.

Column head pressures are used as a surrogate parameter to control HMD emissions.

Essential Potential to Emit (PTE) Parameters

K.1.  Hours of Operation.  This emissions units are allowed to operate continuously, i.e., 8,760 hours/year.

K.2.  All applicable requirements of 40 CFR Part 60 Subpart NNN, Standards for Performance for Volatile Organic Compound (VOC) Emissions for Synthetic Organic Chemical Manufacturing Industry (SOCMI) Distillation Operations, shall be adhered to for EU-041. Subpart NNN requirements that apply include the following:

K.2.a.  A total resource effectiveness (TRE) index shall be maintained at a value greater than or equal to 1.0.  Details of the calculation(s) shall be submitted with any testing required and when any process changes that may impact the TRE index are made.

TRE: >1.

K.2.b.  Continuous monitoring of stripper columns head pressure is required and serves as a surrogate parameter to control HMD emissions.  The column head pressure shall be maintained at or below a maximum of 100mm Hg.  Records of stripper column head pressure logged hourly shall be maintained and be available for inspection by the Department.

[Department approved alternative to 40CFR60.663(d)(2)(i)].

Records: Jan-Aug, 2003—Ok.  At inspection Column B head pressure was 60 mmHg and Column C head pressure was 44 mmHg.

K.3.  Condensation of steam and solution of HMD between stages of a series of steam vacuum jets are determined to be vapor control devices deemed necessary by the Department.  The permittee shall maintain operations and maintenance of the jets and condensers sufficient to provide reasonable assurance that HMD emissions remain approximately at the levels of these measured values. Maintained

#### Test Methods and Procedures

K.4.  Emissions Tests.  See common condition number O.1.

K.5.  HMD test method shall be EPA Methods 1, 2, 4 and 18 or 25A, and ASTM Methods D1946-77 and D2382-76.

K.6.  Determination of Process Variables.  See common condition number O.2.

Accuracy is assured through annual calibration.

Periodic Monitoring

K.7.  EU-041 Head Pressure.   Records of B & C stripper column head pressure logged hourly when the column is in service, shall be maintained and be available for inspection by the Department. Logs Jan-Aug were reviewed and indicate compliance.

NSPS STORAGE TANKS

Subsection N.  This section addresses the following emissions unit.

Emission Unit ID No. 097

| 40 CFR Part 60, Subpart Kb Volatile Organic Liquid (VOL) Tanks Inventory - 5/23/2000 |  |
| --- | --- |
| [for tanks constructed, modified or reconstructed after July 23, 1984, with volumes over 10,600 gallons, |
| which are subject to 40 CFR Subpart Kb, VOL Tank regulations] |  |
| Tank Number | Facility ID Number | Tank Volume (Kgal) | Tank Contents | NSPS Applicability |
| 326TA115A | UIC permit | 1000 | process wastewater | Subject to Kb recordkeeping but exempt due to low vapor pressure of VOC |
| 326TA115B | UIC permit | 1000 | process wastewater | Subject to Kb recordkeeping but exempt due to low vapor pressure of VOC |
| 326TA115C | UIC permit | 1000 | process wastewater | Subject to Kb recordkeeping but exempt due to low vapor pressure of VOC |
| 326TA115D | UIC permit | 1000 | process wastewater | Subject to Kb recordkeeping but exempt due to low vapor pressure of VOC |
| 326TA119 | UIC permit | 6000 | process wastewater | Subject to Kb recordkeeping but exempt due to low vapor pressure of VOC |
| 326TA171 | UIC permit | 12 | process wastewater | Subject to Kb recordkeeping but exempt due to low vapor pressure of VOC |
| 326TA172 | UIC permit | 120 | process wastewater | Subject to Kb recordkeeping but exempt due to low vapor pressure of VOC |
| 403TA50 | 2 | 108.5 | Adipic Glutaric, Succinic acids and water | Subject to Kb recordkeeping but exempt due to size and/or low vapor pressure of VOC |
| 465TA6 | 2 | 300 | Adipic acid, nitric acid , water | Subject to Kb recordkeeping but exempt due to size and/or low vapor pressure of VOC |
| 461TA60 | 20 | 87 | Boric acid and water solution | Subject to Kb recordkeeping but exempt due to size and/or low vapor pressure of VOC |
| 461TA151 | 20 | 60 | KATT residue | Subject to Kb recordkeeping but exempt due to size and/or low vapor pressure of VOC |
| 416TA284D | 40 | 49.5 | Adiponitrile | Subject to Kb recordkeeping but exempt due to size and/or low vapor pressure of VOC |
| 416TA291 | 40 | 49.5 | Adiponitrile | Subject to Kb recordkeeping but exempt due to size and/or low vapor pressure of VOC |
| 442TA33A | 40 | 850 | Adipinitrile | Subject to Kb recordkeeping but exempt due to size and/or low vapor pressure of VOC |
| 442TA33B | 40 | 850 | Adipinitrile | Subject to Kb recordkeeping but exempt due to size and/or low vapor pressure of VOC |
| 486TA19 | 77 | 35.8 | Methanol | Subpart Kb requirements met by use of floating roof design. |
| 416TA316 | 77 | 17.7 | Dimethyl esters | Subject to Kb recordkeeping but exempt due to size and/or low vapor pressure of VOC |
| 416TA470 | 77 | 27 | Dimethyl esters | Subject to Kb recordkeeping but exempt due to size and/or low vapor pressure of VOC |
| 416TA473 | 77 | 18.1 | Dimethyl esters | Subject to Kb recordkeeping but exempt due to size and/or low vapor pressure of VOC |

| 416TA480 | 77 | 17.7 | Dimethyl esters | Subject to Kb recordkeeping but exempt due to size and/or low vapor pressure of VOC |
| --- | --- | --- | --- | --- |
| 416TA482 | 77 | 17.7 | Dimethyl esters | Subject to Kb recordkeeping but exempt due to size and/or low vapor pressure of VOC |
| 443TA001A | 76 | 165 | Maleic Anhydride | Subject to Kb recordkeeping but exempt due to size and/or low vapor pressure of VOC |
| 443TA001B | 76 | 165 | Maleic Anhydride | Subject to Kb recordkeeping but exempt due to size and/or low vapor pressure of VOC |
| 443TA001C | 76 | 83 | Maleic Anhydride | Subject to Kb recordkeeping but exempt due to size and/or low vapor pressure of VOC |
| 445TA024 | 76 | 105 | Process Oil | Subject to Kb recordkeeping but exempt due to size and/or low vapor pressure of VOC |
| 445TA067A | 76 | 62 | Maleic Anhydride | Subject to Kb recordkeeping but exempt due to size and/or low vapor pressure of VOC |
| 445TA067B | 76 | 62 | Maleic Anhydride | Subject to Kb recordkeeping but exempt due to size and/or low vapor pressure of VOC |
| 445TA085A | 76 | 37 | Maleic Anhydride | Subject to Kb recordkeeping but exempt due to size and/or low vapor pressure of VOC |
| 445TA085B | 76 | 37 | Maleic Anhydride | Subject to Kb recordkeeping but exempt due to size and/or low vapor pressure of VOC |

The following specific conditions apply to the emissions unit listed above:

Essential Potential to Emit (PTE) Parameters

N.1.  Hours of Operation.  These emissions units may operate continuously, i.e., 8,760 hours/year.

Emission Limitations and Standards

N.2.  NSPS Provisions.  The owner or operator of each storage vessel shall keep readily accessible records showing the dimension of the storage vessel and an analysis showing the capacity of the storage vessel for the life of the source.

The records concerning these tanks were reviewed during the previously and found to meet requirements.  No changes have been made since.

Common Conditions

Subsection O.  Common Conditions.

{Permitting Note: The following conditions are placed here as a convenience and to avoid duplication.  See specific conditions in Subsections A through N for applicability.}

O.1.  Test Methods and Procedures

Emissions tests are required to show continuing compliance with the standards of the Department.  The test results must provide reasonable assurance that the source is capable of compliance at the permitted maximum operating rate.  Tests shall be conducted annually, unless otherwise specified in specific conditions.  Results shall be submitted to the Department within 45 days after testing.  The Department shall be notified at least 15 days prior to testing to allow witnessing.

Testing of emissions shall be conducted with the emissions unit operating at permitted capacity, which is defined as 90 to 100 percent of the maximum operation rate allowed by the permit.  If it is impracticable to test at permitted capacity, an emissions unit may be tested at less than the minimum permitted capacity (i.e., at less than 90 percent of the maximum operation rate allowed by the permit); in this case, subsequent emissions unit operation is limited to 110 percent of the test load until a new test is conducted, provided however, operations do not exceed 100 percent of the maximum operation rate allowed by the permit.  Once the emissions unit is so limited, operation at higher capacities is allowed for no more than 15 consecutive days for the purpose of additional compliance testing to regain the authority to operate at the permitted capacity.

O.2.  Determination of Process Variables.

The owner or operator of an emissions unit for which compliance tests are required shall install, operate, and maintain equipment or instruments necessary to determine process variables, such as process weight input or heat input, when such data are needed in conjunction with emissions data to determine the compliance of the emissions unit with applicable emission limiting standards.

Equipment or instruments used to directly or indirectly determine process variables, including devices such as belt scales, weight hoppers, flow meters, and tank scales, shall be calibrated and adjusted to indicate the true value of the parameter being measured with sufficient accuracy to allow the applicable process variable to be determined within 10% of its true value.