| ### SECTION IV: COMMENTS |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Facility Name: | Gulf Power Company, Crist Plant | Title V: | Y | AIRS ID: | 0330045 |  |
| INSPECTION DATE: | August 7, 2003 |  |  |  |  |  |
| To support Compliance or Noncompliance status of emission units, include additional comments and supporting records logs, reports or data below, or as attachments to the report. |  |  |  |  |  |  |
| COMMENTS: |  |  |  |  |  |  |

Plant Walkthrough:  Unit 1 has been decommissioned.  Units 2 and 3 were not operating.  Mr. Beaty said that they ran less than 100 hours in 1CY03 and did not run at all in 2CY03.  They are to be decommissioned in 2005.  Current data output from the NOx, SO2 and opacity monitors for Units 4, 5, 6 and 7 indicated compliance.  Operating and maintenance records were reviewed in the CEMS shelters.  These records indicate the required quality control procedures are followed and malfunctions are addressed in a timely manner.  Construction for the new electrostatic precipitator is well underway.

Testing:  Required annual testing has been completed except for SO2 testing on Unit 6.  Unit 6 SO2 testing is scheduled to be completed by the end of September 2003. Unit 7 RATA and SO2 testing was completed April 15, 2003.  Inadvertently, the test report was not sent to the Department.  During the inspection, a copy was requested. It was received Aug 11.  A review of this test report indicated compliance with emission limits.  The Unit 7 compliance status is shown as minor noncompliance (MNC) for late reporting.

Fly Ash Storage Silos (EU 008):  Each silo has a baghouse with 2 vents each.  The VE limit is 20% for each vent. In the past, some VE tests have been reordered using one form for each silo with a comment that no emissions were seen.  Since each vent has a limit, a VE is required for each.  Please ensure that future VE tests for this emission unit are recorded using one VE form for each vent.

Carbonaceous Material Burning:  Mr. Beaty said the testing of Crist Plant Unit 4 for burning carbonaceous material has been completed and that Gulf Power determined that it was not beneficial to burn it.

Compliance Assurance Monitoring (CAM): Gulf Power has been conducting a series of tests at all of its plants to gather data for the development of a CAM protocol to be submitted with the Title V renewal applications in 2004.

Periodic Monitoring: Particular matter (PM) monitoring is done using Continuous Opacity Monitoring Systems (COMS).  For any calendar quarter in which more than 5% of the COMS reading show 20% or greater opacity, a PM test shall be conducted during the following calendar quarter. Unit 5 has opacity readings of 5.1% during the previous quarter.  It is scheduled for testing in late August.

Plant Records Review:  Records are maintained as required for continuous monitoring systems, for used oil burned and an analysis of its contents, for fuel used, heat and sulfur content and hours operated on each fuel.  Records indicated compliance.

Department File Review:  The Annual Operating Report, Statement of Compliance, Quarterly Excess Emissions/SO2 Emissions Summary Report and CEM Summary Report were received in a timely manner and indicated compliance.