June 27, 2003

R. Mark Triplett, P.E., Director

Department of Solid Waste Management

Escambia County

13009 Beulah Road

Cantonment, Florida 32533-8831

Dear Mr. Triplett:

Department representative Charles Norman inspected the Perdido Landfill, I.D. 0330246, on June 17, 2003.  He inspected only those activities covered by the Air Resources Management Program.  He found the facility to be in compliance.  A copy of the Electronic Access System for Inspection Information Retrieval (EASIIR) inspection report is enclosed.  A summary of the inspection follows.

- Active Gas Collective System:  Extractions are configured with the proper ports for measuring the landfill gas concentrations of nitrogen and oxygen, well temperature and well pressures.  A review of records on site indicated that problems found were addressed and appropriate actions were taken within the permitted time limits.  Onsite records contain the installation date and location of each well.  Records and modeling indicate the wells are of sufficient density.  The landfill gas handling system is designed to handle 2,800 scfm.  This capacity is sufficient to meet the expected generation rate including the new cell now under construction.

- Flare:  The flare was not operating at the time of the inspection.  A review of onsite operating procedures and records of flare operation indicated compliance with permitted conditions.  A thermocouple is used to monitor the flare operation and a strip chart continuously records the temperature.  During periods when the gas was not sent to International Paper, either the field was shut down temporarily or the gas was flared.

- Landfill Surface Monitoring:  The landfill surface concentrations are monitored on a quarterly basis.  Records indicate surface exceedances were addressed, problems corrected and monitoring redone within the allowed time limits.

- Landfill Boundary Monitoring:  Eight boundary monitors are used to monitor offsite migration of landfill gas.

- Asbestos:  No areas of the landfill gas collection were excluded based on the presence of asbestos.  Asbestos-containing areas are mapped.

- Reports:  The Annual Operating Report, Annual Statement of Compliance, and Administrator’s Annual Report were received and reviewed by the Department.  These reports contained the required information and indicate compliance with permit conditions.

R. Mark Triplett, P.E.

Page Two

The draft for the new Title V permit has been completed and is being reviewed by EPA.  The EPA comment period will end August 3, 2003.  The landfill is now subject to NESHAP Subpart AAAA, National Emission Standards for Hazardous Air Pollutants:  Municipal Solid Waste Landfills.  The compliance date is January 16, 2004.  There are three changes of note to the new Title V permit:

- The Administrator’s report will become a semiannual report.  Mr. Hixson has suggested that the report be made on a CD since the report is voluminous.  We recommend that the next report be submitted in hardcopy form along with a disk for evaluation.

- A startup, shutdown, malfunction plan (SSMP) will be required.  Mr. Ellis said Biomass is working on a plan.

- Annual visible emissions testing of the flare will be required using EPA Method 22.

If you have any questions or comments, please contact Mr. Norman at 595-8364, extension 1222.

Sincerely,

Sandra F. Veazey

Air Program Administrator

SFV:cnc

Enclosure