DATA COLLECTION MATRIX FOR HILLSBOROUGH COUNTY RRF

| PARAMETER | UNIT 1 | UNIT 2 | UNIT 3 |
| --- | --- | --- | --- |
| Tons/day (4-hr block avg) 460 (also limited to rolling 52-week avg of 1200 tpd for whole facility) |  |  |  |
| Steam rate limit (lesser of 102,000 lb/hr or 110% of rate from last test) | 102,000 | 102,000 | 102,000 |
| Steam rate observed | 94 | 97 | 91 |
| Maximum baghouse inlet temperature from dioxin test | 331F | 331F | 331F |
| Observed baghouse inlet temperature | 291 | 290 | 296 |
| Minimum carbon injection rate from dioxin test (lb/hr) | 12.5 | 12.5 | 12.5 |
| Observed carbon injection rate | 13.0 | 13.0 | 13.0 |
| NOx (205 ppmv @ 7% O2) | 179 | 152 | 178 |
| CO (100 ppmv @ 7% O2) | 24 | 26 | 18 |
| SO2 (29 ppmv @ 7% O2) | 0 | 1 | 1 |
| SO2 removal (75%) | 100 | 100 | 92 |
| Opacity (10%) | 0 | 0 | 1 |