FLORIDA DEPARTMENT OF ENVIRONMENTAL PROTECTION

INSPECTION REPORT FORM

AIR POLLUTANT EMISSION SOURCES

| FACILITY: Gulf Power - Scholz Plant | DISTRICT: Northwest | COUNTY: Jackson |
| --- | --- | --- |
| ADDRESS: 1460 Gulf Power Road | PHONE: (850) 593-6421 | CONTACT: Kenton Peacock |
| CONTACT OR FACILITY EMAIL ADDRESS: |
| ARMS I.D. #: 0630014 | PERMIT: 0630014-005-AV | EXPIRES: 12/31/2009 |
| RENEWAL APPLICATION/NOTIFICATION DUE DATE: 07/05/2009 |
| SOURCE DESCRIPTION: Commercial Power Generation Facility |
| INSPECTED BY: Richard Brookins INSPECTION DATE: 08/30/2006 | AUDIT TYPE: Ins2 | COMPLIANCE STATUS: MNC |

INSPECTION COMMENTS

I was accompanied on this inspection by Mr. Marc Sumner of the Industrial Waste Section.  We arrived at the facility and were greeted by Mr. Alan McLane representing Plant Scholtz and Mr. Mike Kyhos representing Gulf Power Corporate Environmental Affairs.  Both Mr. McLane and Mr. Kyhos provided access to requested records and accompanied me during my inspection of the facility, along with Mr. Sumner.  This was a notified, scheduled inspection.  Compliance testing for SO2 and particulate was being performed during this inspection.

Facility-wide Conditions

There were no objectionable odors noticed during the inspection.  [Facility-wide Condition 2]

The facility does not have a Risk Management Plan as it is not required.  It does however have a full set of safety and environmental procedures, along with Best Management Practices (BMP’s) and Emergency Response guidelines.  [Facility-wide Condition 3]

VOC control at the facility appears adequate.  [Facility-wide Condition 6]

There were no fugitive emissions greater than 20% opacity noted during the inspection.  [Facility-wide Condition 7]

Reasonable Precautions are judged to be adequate.  The coal pile is packed routinely and water is used as a dust suppressant on the roadways as necessary.  Grass is maintained over the ash disposal site.  [Facility-wide Condition 8]

This facility has a high chain link fence surrounding the property.  Security cameras along with “No Trespassing” signs are posted around the perimeter.  [Facility-wide Condition 13]

## Emission Unit 001 – Number 1 Power Boiler

This emission unit is a power boiler used for producing steam to make electricity.  Allowable fuels include coal, fuel oil, on-spec used oil, and oil contaminated soil.  This emission unit is a Phase II Acid Rain Unit.

An hourly record of operating hours on various fuels is maintained.  Completed daily log sheets are submitted to the Plant Environmental office.  These log sheets were reviewed as part of this inspection.  According to information supplied during the inspection this Emission Unit has operated for a total of 4,818 hours during the first half of 2007.   [Specific Condition A.4]

This emission unit has a Visible Emission limit of 40% opacity.  Opacity at the time of inspection was 3.1 % according to the control room readout.  [Specific Condition A.5]

This emission unit is allowed to operate for 3 hours in any 24 hour period at up to 60% opacity during soot blowing and load changing operations.  According to the supplied information this emission unit has operated 3.0 percent of the time with greater than 20 percent opacity during the previous quarter.  [Specific Condition A.6]

This emission unit has an SO2 emission limit of 6.17 lbs/MMBtu when operating on coal or a limit of 2.75 lbs/MMBtu when operating on oil.  According to the control room instrumentation this emission unit was operating on coal with an emission rate of 1.884 lbs/MMBtu at the time of inspection.  [Specific Condition A.9 & Specific Condition A.10]

Fuel oil analyses were available for review during this inspection.  [Specific Condition A.16]

A SO2 Continuous Emission Monitoring System (CEMS) is installed on this emission unit.  A new SO2 CEMS has been installed in the common stack and the CEMS located in the ductwork are now considered “Process Instrumentation” according to facility personnel. Data availability has been such that “As-fired” fuel sampling has not been required.  The CEM Quality Control Program was available for, and reviewed as, part of this inspection.  [Specific Condition A.22 & Specific Condition A.24]

Composite fuel samples are taken daily to determine the HHV of the fuel.  Heat input calculations are performed after receiving the results of the analysis.  These records were available and reviewed as part of this inspection.  [Specific Condition A.25 & Specific Condition A.32]

Instrumentation is calibrated and maintained as appropriate.  An electronic maintenance management (Work Order) program is utilized to schedule and track required maintenance. [Specific Condition A.27]

The facility is required to maintain a maintenance log for the CEM system.  This log was available and reviewed as part of the inspection.  [Specific Condition A35]

The facility is permitted to burn “On-spec” used oil for energy recovery.  A review of the records showed that a load of used oil was burned on June 11, 2007 without a total quantity of oil burned being recorded.  However from the size of the tank it is known that this amount could not have exceeded 500 gallons.  [Specific Condition A.37 – Failure to maintain required records]

The facility has a CAM (Compliance Assurance Monitoring) plan.  As part of this plan a one hour excursion is defined as being above 14% opacity, with a three hour excursion being defined as over 16 % opacity.  According to the control room readout 3.0 % of the opacity readings have been over 14 % opacity for the current quarter.  [Specific Condition A.38]

## Emission Unit 002 – Number 2 Power Boiler

This emission unit is a power boiler used for producing steam to make electricity.  Allowable fuels include coal, fuel oil, on-spec used oil, and oil contaminated soil.  This emission unit is a Phase II Acid Rain Unit.

An hourly record of operating hours on various fuels is maintained.  Completed daily log sheets are submitted to the Plant Environmental office.  These log sheets were reviewed as part of this inspection.  According to information supplied during the inspection this Emission Unit has operated for a total of 4,785 hours during the first half of 2007.   [Specific Condition A.4]

This emission unit has a Visible Emission limit of 40% opacity.  Opacity at the time of inspection was 4.6 % according to the control room readout.  [Specific Condition A.5]

This emission unit is allowed to operate for 3 hours in any 24 hour period at up to 60% opacity during soot blowing and load changing operations.  According to the control room readout, this emission unit has operated over 20 percent opacity during the present quarter.  [Specific Condition A.6]

This emission unit has an SO2 emission limit of 6.17 lbs/MMBtu when operating on coal or a limit of 2.75 lbs/MMBtu when operating on oil.  According to the control room instrumentation this emission unit was operating on coal with an emission rate of 1.817 lbs/MMBtu at the time of inspection.  [Specific Condition A.9 & Specific Condition A.10]

As previously mentioned, fuel oil analyses were reviewed during for this inspection.  [Specific Condition A.16]

A SO2 Continuous Emission Monitoring System (CEMS) is installed on this emission unit.  As previously mentioned, a new SO2 CEMS has been installed in the common stack and the CEMS located in the ductwork are now considered “Process Instrumentation” according to facility personnel. Data availability has been such that “As-fired” fuel sampling has not been required.  The CEM Quality Control Program was available for, and reviewed as, part of this inspection.  [Specific Condition A.22 & Specific Condition A.24]

Composite fuel samples are taken daily to determine the HHV of the fuel.  Heat input calculations are performed after receiving the results of the analysis.  These records were available and reviewed as part of this inspection.  [Specific Condition A.25 & Specific Condition A.32]

Instrumentation is calibrated and maintained as appropriate.  An electronic maintenance management (Work Order) program is utilized to schedule and track required maintenance. [Specific Condition A.27]

The facility is required to maintain a maintenance log for the CEM system.  This log was available and reviewed as part of the inspection.  [Specific Condition A35]

The facility is permitted to burn “On-spec” used oil for energy recovery.  According to the supplied information this emission unit has burned 980 gallons of used oil this current YTD.  Oil analyses were reviewed as part of this inspection and found to be in-compliance with required specifications..  [Specific Condition A.37]

The facility has a CAM (Compliance Assurance Monitoring) plan.  As part of this plan a one hour excursion is defined as being above 14% opacity, with a three hour excursion being defined as over 16 % opacity.  According to the control room readout 5 % of the opacity readings have been over 14 % opacity for the current quarter.  [Specific Condition A.38]

RECOMMENDATIONS:

Ensure all quantities of used oil burned for energy recovery are recorded as required by permit conditions.

Copy the Panama City Branch Office on all compliance related notifications as discussed during the inspection.