May 1, 2007

Mr. Achaya Kelapanda

District Manager

Springhill Regional Landfill

4945 Hwy 273

Graceville, Florida 32440

Dear Mr. Kelapanda:

A Department representative recently inspected your facility.  A copy of the inspection report is enclosed.  Please note the permit expiration date and renewal application due date shown on the report.

This letter applies only to activities covered by the Air Resources Management Program.  It indicates compliance at the time of inspection for those sources specifically listed on the inspection report.

If you have any questions, please contact Richard Brookins at 850/872-4375, extension 108 or Richard.Brookins@dep.state.fl.us.

Sincerely,

Marlane Castellanos

Branch Office Manager

FLORIDA DEPARTMENT OF ENVIRONMENTAL PROTECTION

INSPECTION REPORT FORM

AIR POLLUTANT EMISSION SOURCES

| FACILITY: Springhill Regional Landfill | DISTRICT: Northwest | COUNTY: Jackson |
| --- | --- | --- |
| ADDRESS: 4945 Hwy 273 | PHONE: (850) 263-7100 | CONTACT: Achaya Kelapanda or Jeff Massey |
| CONTACT OR FACILITY EMAIL ADDRESS: akelapanda@wm.com |
| ARMS I.D. #: 0630045 | PERMIT: 0630045-006-AV | EXPIRES: 02/13/2009 |
| RENEWAL APPLICATION/NOTIFICATION DUE DATE: 08/17/2008 |
| SOURCE DESCRIPTION: Class I landfill |
| INSPECTED BY: Richard Brookins INSPECTION DATE: 04/24/2007 | AUDIT TYPE: Ins2 | COMPLIANCE STATUS: In Compliance |

INSPECTION COMMENTS

I arrived at the facility and was greeted by Mr. Achaya Kelapanda, District Manager.  Mr. Kelapanda and I discussed the operations of both the facility and the new landfill gas electric generating plant.  According to Mr. Kelapanda, initial operation of the electric generating plant occurred on April 25, 2006 and the emission units have been operating satisfactory ever since.  We then proceeded with the record review and site inspection.  Mr. Kelapanda provided copies of requested records and accompanied me during the inspection of the facility.  The facility is currently constructing a new cell beginning with the installation of the liner.

There were no objectionable odors noticed during the inspection.  The facility continues to appear to be pro-active regarding odor control.  [Facility-wide Condition 2]

There were no fugitive visible emissions in excess of 20% noticed during the inspection.  [Facility-wide Condition 3]

The water tanker was in operation and the roads were sufficiently wet. Speed limits are posted for the facility and traffic appeared to be complying with the posted limits.    [Facility-wide Condition 7]

An Annual Statement of Compliance was timely submitted to the Department.  [Facility-wide Condition 9]

There was no open burning observed during the inspection.  [Facility-wide Condition 14]

Asbestos disposal records are maintained and were reviewed as part of this inspection.  Copies of the current year-to-date records were supplied when requested.  GPS is used to determine the actual physical disposal location and noted on each record as to coordinates and height (depth).  This is done for all loads of ACM, both friable and non-friable.  Twenty-four hour advance notification is required so the disposal hole can be prepared ahead of time.  After the vehicle dumps its load the hole is immediately refilled with MSW and is then covered with 6” of soil at the end of the working day.  Procedures are in place to handle any discrepancies in the manifesting or containment of the waste material.   [Facility-wide Condition 15]

## EU-001	 North Landfill Gas Collection and Control System

The former flare unit for this emission unit has been decommissioned and all landfill gas now goes to the electric generating system.

The facility is required to recalculate the NMOC annually and the results were timely submitted to the Department.  [Specific Condition A.3]

Surface concentrations of methane are monitored as required.  A serpentine pattern around the cell is traversed with the paths being approximately 100” apart.  According to the facility, there have been no methane concentration exceedences and the facility continues to monitor annually.  Surface concentration of methane was last monitored on 03/30/2007 with no exceedences noted.   [Specific Condition A.5]

Operations and maintenance records for the gas collection system for the current year-to-date were reviewed as part of this inspection.  Each wellhead has an isolation valve, sampling port, and temperature indicator as required.  The gas collection header pressure, oxygen concentration, and temperature of the landfill gas are recorded monthly.  [Specific Condition A.6]

The facility submits semi-annual deviation reports to the Department.  The most recent report covered the period July 2006 thru December 2006 and was timely submitted to the Department.  [Specific Condition A.7]

The landfill gas collection wells are constructed from PVC material.  Other non-porous, corrosion resistant materials are also used as necessary.  Isolation valves are installed at each well as required.  [Specific Condition A.8]

## EU-004	 South Landfill Gas Collection System

The former flare for this emission unit has been relocated to the electric generating plant and now serves as a backup to that system in the event of failure or extended maintenance.

Current year-to-date operations and maintenance records for this gas collection system and flare unit were also reviewed as part of this inspection.  Each wellhead has an isolation valve, sampling port, and temperature indicator as required.  The gas collection header pressure, oxygen concentration, and temperature of the landfill gas are recorded monthly. Surface concentrations of methane are monitored as required.  A serpentine pattern around the cell is traversed with the paths being approximately 100” apart.  According to the facility, there have been no methane concentration exceedences.  Surface concentration of methane was last monitored on 04/19/2007 with no exceedences noted.   [Specific Condition B.5]

Semi-annual NMOC emission rate reports are now required for this emission unit.  This report covering the period July 2006 thru December 2006 was timely submitted to the Department.  The facility also submits semi-annual deviation reports to the Department as required.  The most recent report covered the period July 2006 thru December 2006 and was timely submitted to the Department.  [Specific Condition B.6]

Copies of the P.E. certified design and calculations for the gas collection system are maintained at the facility.  The landfill gas collection wells are constructed from PVC material.  Other non-porous, corrosion resistant materials are also used as necessary.  Isolation valves are installed at each well as required.  [Specific Condition B.7]

NMOC emission rate reports are required.  These reports were timely submitted to the Department and a copy was available for review during the inspection.  [Specific Condition B.8]

### EU-002	 Solidification Process

The flyash baghouse appeared to be in good operating condition.  Maintenance was being performed during this inspection with all bags being replaced.  Since there were no flyash unloading or mixing operations occurring during this inspection, the VE was 0 % from this Emission Unit.  [Specific Condition C.4]

A Method 9 Visible Emission evaluation is required to be performed annually during each federal fiscal year.  This evaluation was last performed on 04/26/2006.  [Specific Condition C.5]

Common Conditions

Operating records for both landfill gas systems for the current year-to-date were reviewed as part of this inspection.  Oxygen was less than 5% as required and temperatures were below the maximum allowed.  As mentioned previously, surface concentrations of methane are evaluated quarterly (or annually) as required.  Flare flame temperatures are monitored on both units and the control systems are designed to stop the gas mover system and close the isolation valve upon loss of flame temperature.  [Specific Condition D.2]

Documented monthly inspections of the cover integrity are performed.  The results of these inspections were available for review at the time of inspection.  [Specific Condition D.3]

Records were available showing the maximum design capacity, current amount of solid waste in place, and projected waste acceptance rates were available and reviewed as part of the inspection.  Drawings showing the location, installation date and unique ID number for each well were also available reviewed.  [Specific Condition D.4]

EU-005 Landfill Gas Treatment / Electric Generating Plant

Six of the authorized eight electric generating units have been installed and are currently operating.  The facility was producing 3.9 MW of power with a landfill gas flow rate of 1900-2000 CFM at the time of the inspection.  The facility normally produces 4.5 MW of power but one of the engines had been down for maintenance and was just resuming operations.  These emission units began initial operations on April 25, 2006 and the initial emission testing was performed with the results timely submitted to the Department.

Inspection and operating records for this emission unit are maintained and were reviewed as part of this inspection.  [Specific Condition F.6]

A flow meter going to the flare unit is installed and the required records are maintained in the event of flare usage.   The flare isolation valve is designed to automatically close in the event of any significant drop in flare temperature.  A Method 22 for this system was last performed on 04/18/2006.   [Specific Condition F.7]

RECOMMENDATIONS:

1.	Conduct annual Method 9 visible emission testing as required for the solidification basin.  Notify the Department at least 15 days prior to conducting these tests.