# INSPECTION REPORT

# AIR POLLUTANT EMISSION SOURCES

| FACILITY Florida Power & Light, Manatee Plant | DISTRICT Southwest | COUNTY Manatee |
| --- | --- | --- |
| ADDRESS Highway 62, 5 miles east of US 301 Parrish FL | CONTACT(S) Mary Maxwell (941) 776-5278 (plant environmental contact) Lynn French |
| AIRS ID # 0810010 | PERMIT # 0810010-010-AC 0810010-011-AV | EXPIRATION DATES 12/31/08 | ARMS ENTRY DATE |
| SOURCE DESCRIPTION Steam electric generating plant. Burns natural gas, No. 6 residual fuel oil, No. 2 fuel oil, propane, or used oil from FP&L operations. |
| INSPECTION DATE 4/30/07 | AUDIT TYPE II-CDS | COMPLIANCE STATUS In compliance |
| INSPECTION FINDINGS |
| PARAMETER | PERMITTED VALUE | OBSERVATIONS |
|  |  | Unit 1 | Unit 2 |
| 1. Heat input, fuel oil, MMBtu/hr (Specific Condition A.1 (SC A.1)) | 8650 MMBtu/hr 5670 MMBtu/hr when firing natural gas alone | See Comments | See Comments |
| 2. Fuel used (SC A.3) | Natural gas, No. 6, No. 2, propane, or used oil from FP&L operations. No used oil during startup. | In compliance | In compliance |
| 3. Emission limits: (SC A.5-A.10) a. Opacity, steady state b. Opacity, soot blowing/load change c. PM d. NOx e. SO2 | 40% 60% <3 hr in 24 hr with <four 6-min periods of <100% 0.1 lb/MMBtu normal; 0.3 lb/MMBtu soot blowing/load change 0.30 lb/MMBtu, 30-day rolling avg. as measured by CEMS <1.0% sulfur content in fuel oil | See Comments | See Comments |
| 4. Determination of Process Variables (SC A.16) | Install, operate, and maintain a system to continuously monitor and record the amount of natural gas consumption and heat input. This system shall be designed to interact with the existing continuous emissions monitors. | In compliance | In compliance |
| 4. Fuel restrictions (SC A.37) Arsenic Cadmium Chromium Lead PCBs Total halogens Total oil (both units) | (used oil only) 5 ppm 2 ppm 10 ppm 100 ppm 50 ppm 1000 ppm 40000 gallons | Batch dated: No used oil burned | Batch dated: No used oil burned |
| 5. Disposal of spent boiler-cleaning chemicals | Non-hazardous chemicals may be disposed of through injection into the boiler. Samples must be analyzed and confirmed non-toxic. Quantity cannot exceed 50 gpm and may not be injected during start-up; normal boiler temperature must be maintained. Records of date, start and stop times, and quantity disposed must be kept for 3 years. | No spent boiler cleaning chemicals were burned in 2006 or so far in 2007. |
| INSPECTOR(S) NAME(S) Bill Shroeder / Bret Galbraith |
| SIGNATURE(S) | DATE |