Continuation of Inspection Comments for Orlando Cogen, 0950203:

Subsection C. Includes Emission Units 001, 002

C.1. is a definition of the various provisions of 40 CFR 60.

C.2. states that all operators and supervisors shall be properly trained.

C.3. limits the operating rate based on stack testing data.  The CT is allowed to operate at the permitted rate of 980 MMBtu/hr LHV at ISO conditions.  The DB is limited to a maximum heat input rate of 115.7 MMBtu/hr LHV.

C.4. states that only natural gas shall be burned in these units.  Only natural gas is used at Orlando Cogen.  Florida Gas Transmission supplies the natural gas via the pipeline.

C.5. states when both the CT and the DB are operating, NOX emissions shall not exceed 15 ppmvd (30 day rolling average) @ 15% O2.  A report was given to the inspectors for 10/20/08 when the CT and DB ran together.  The 30 day rolling average was 13.7 ppmvd @ 15% O2.  This is below the permit limit of 15 ppmvd @ 15% O2.

C.6. states that the owner or operator must not discharge into the atmosphere for the CT any gases which contain SO2 in excess of 0.90 pounds per megawatt-hour.  The condition also states the owner or operator must not burn in the CT any fuel which contains potential sulfur emissions in excess of 0.06 pounds SO2 per MMBtu heat input.  The facility obtains the daily stream history titled “Total Sulfur Previous Day.”  This data is placed on a chromatograph, according to Mr. Good.  The natural gas comes from the Brooker 24” Stream.  The values in the report are in parts per million (ppm) and in grains/hcf.  The highest observed ppm sulfur for 2/26/09 was 2.29 ppm.  The AOR should reflect 1.6 mass tons of SO2 emitted.

C.7. states the combustion control shall be utilized for CO control.  Future installation of an oxidation catalyst may be installed pending performance testing results and cost/benefit analysis of using such control.

C.8. states that excess emissions are allowed for two hours in any 24 hour period.  No excess emissions were reported, except for the gas valve mapping granted by the FDEP.

C.9. For this condition, no excess emissions were reported from poor maintenance, poor operation, or any other equipment or process failure.

C.10. states NOX excess emissions and monitor downtime must be reported as described in 40 CFR 60.4385.  The facility submits this report to OCEPD, as required.

C.11. states SO2 excess emissions and monitor downtime must be reported as described in 40 CFR 60.4385.  The facility submits this report to OCEPD, as required.

C.12. states data can be excluded from the CEMS compliance demonstration during the dry low NOX (DLN) tuning event.  Tuning of the DLN burners did not occur this year.

C.13. The CEM is calibrated, maintained and operated in the stack to measure NOX emissions.  The CEMS complies with the 40 CFR 60, Appendix B, Performance Specification 2.  The CEM also meets the requirements in 40 CFR 60.4345.

C.14 The CEM compliance demonstration occurs when NOX emissions are less than or equal to 63.1 lb/hr when only the CT is operating and less than or equal to 75.3 lb/hr when both the CT and DB are operating.  Records demonstrated the CEM was in compliance with this requirement.

C.15. Test methods required are listed in this condition.  The next compliance test will be scheduled on 4/7/09-4/8/09, according to Mr. Good.

C.16-C.22 are related to annual compliance testing requirements.  This facility plans to conduct the next compliance test on 4/7/09-4/8/09.

C.23. contains a reporting schedule for specific reports required by the facility to submit to the Compliance Authority.  These reports are received by OCEPD, as required.

C.24. requires 15 day notification prior to the compliance test date.   The facility submits this notification, as required.

C.25. states the facility shall notify OCEPD in case of excess emission resulting from malfunctions.  There have been no incidents this past year.

C.26. requires the facility to submit reports annually for five years following the turbine upgrade to state the project did not increase CO and NOX emissions.  The facility has submitted the first report, as required.  The CT was upgraded in 2008.

Section IV. Acid Rain Part

Conditions A.1-A.5 are related to the Acid Rain Program.  The facility submitted the Phase II Acid Rain Part application and submitted it, as required.  The SO2 allowances in the chart are for the years 2009-2013.  All of the allowances are zero, according to the chart in the permit.

The facility is also subject to 40 CFR 60 Subpart KKKK_ Standards of Performance for Stationary Combustion Turbines.  According to Table 1 to Subpart KKKK, the facility is complying with this Subpart by accepting the NOX emission standard of 15 ppm @ 15% O2.

The facility appears to be in compliance with all of their permit conditions at this time.