| FACILITY INFORMATION |
| --- |
| Facility Name: Lake Worth Utilities |
| ARMS ID No.: 099-0045 | Air Permit No.: 099-0045-003-AV | Expiration Date: 12/31/2012 |  |
| Facility Contact: Mike Ridge Email: Mridge@lakeworth.org | Title: Environmental Performance Specialist |

| Inspection Summary |
| --- |
| Inspection Date: 06/30/2010 | Inspector: Paul Kalamaras/Binod Basnet/Laxmana Tallam |
| Report Date: | Signature: |
| Inspection Type: Full Compliance Evaluation onsite | Inspection Subtype: FCS |
| Compliance Status; IN | ARMS Updated: Yes | Approval/Date: |
| Facility Overview: Facility Wide Conditions: In MNC SNC Are pollutant emission standard for objectionable odor met? Y Conditions: Are requirements to prevent unconfined particulate matter Y properly maintained and visible standard met? Conditions: Are conditions for unregulated emissions units and activities met? Y Conditions: Are conditions for insignificant emission units and activities listed? Y Condition: Are general pollutant emission standard for VOC’s met? Y Conditions: Are general pollutant emission limiting standard for organic solvent met? Y Condition: |

Lastpage

| Emission Unit Inspection Details |
| --- |
| EU No. | Compliance In or Out | Inspection Observations and Comments |
| FAC EU1,2 3,4,5 | IN IN | No. 5 fuel oil sulfur content shall not exceed 2.25% by weight. - No. 5 = 1.7 % on 04/14/2010 No. 2 fuel oil sulfur content shall not exceed 0.35% by weight. - No. 2 = 0.0128% on 04/14/2010 Five 2000KW diesel generators. All are model 567D4 by GM Electro Motive Division - NOx testing required if operated only on fuel oil more than 400 hours/year: MU1 29hrs MU2 22hrs MU3 272hrs MU4 89hrs MU5 346hrs Limit = 8,760 hours All under 400 hrs No test required. |
| EU6 | IN | Gas Turbine #1 (GT-1). 30MW / 435mmBtu/hr. No. 2 fuel oil only. - NOx testing required if operated only on fuel oil more than 400 hours/year: 2009 – Operated 8 hours. No testing required. Limit = 8,760 hours - Excess emissions reports submitted in quarterly report? Yes, submitted Jan-Mar 2010 |
| EU7 | IN | Removed. Not returnable to service. |
| EU9 | IN | Fossil Fuel Steam Generator (S-3). 26.4MW / 325.1mmBtu/hr. Natural Gas & No. 6 Fuel Oil Capable. - NOx CEMS required based on a 30-day rolling average except periods of startup, shutdown, & Malfunctions. CEMS average for the last 6 months (12/1/09 - 05/30/10) 0.25 lb/mmBtu on natural gas. Limit = 0.50 lb/mmBtu on natural gas - PM & VE tests required if operated only on fuel oil of more than 400 hours/year. 2009 – Operated 115 hours on natural gas. Testing required.? No. Limit = 8,760 hours |
| EU10 | IN | Removed. Not returnable to service. |
| EU11 FAC Wide | IN IN | Combined Cycle Unit. GT-2/S-5. 29.5MW. Consists of Turbine G-2 at 20MW & Steam Generator S-5 at 10MW. Natural gas & No. 2 Fuel Oil Capable. - NOx & VE testing not required if operated on fuel oil less than 400 hours/year: 2009 – Operated 566 hours on natural gas. Testing is required?. Yes - Last NOx test date = 09/10/09. Actual value = 0.34 lb/mmBtu. Limit = 0.50 lb/mmBtu for natural gas & 0.90 lb/mmBtu for No. 2 fuel oil. - Last VE test date = 09/10/09. Actual value = 0%. Limit = 20% opacity except for (1) 2-min period/hr up to 40%. - Hours of operation per year = 566 hours. Limit = 8,760 hours Conducted on site inspection of entire facility. Reviewed logs and records of operating records and fuel sample reports as well as CEMS data. All were in compliance. |

Lastpage