DATA COLLECTION MATRIX FOR PASCO COUNTY RRF

| PARAMETER | UNIT 1 | UNIT 2 | UNIT 3 |
| --- | --- | --- | --- |
| Tons/day (350, 4-hr block avg) | 58.3 | 58.3 | 58.3 |
| Steam rate limit from last test (lb/hr) | 100,000 | 100,000 | 100,000 |
| Steam rate observed | 90.3 | 90.3 | 90.4 |
| Maximum baghouse inlet temperature (F) | 321 | 321 | 321 |
| Observed baghouse inlet temperature | 290 | 290 | 290 |
| Minimum carbon injection rate from dioxin test (lb/hr) | 15 | 15 | 15 |
| Observed carbon injection rate | 15.6 | 15 | 15 |
| NOx (205 ppmv @ 7% O2) | 190 | 191 | 188 |
| CO (100 ppmv @ 7% O2, 4-hr block avg) | 12 | 19 | 12 |
| SO2 (29 ppmv @ 7% O2, 24-hr geometric mean) | 0 | 0 | 1 |
| SO2 removal (75%) | 100% | 100% | 98.3% |
| Opacity (10%) | 0 | 1 | 0 |

Note:  Limits updated after 2003 stack tests.