| 1030019 84701 |  |
| --- | --- |
| FACILITY: Honeywell International, Inc. | PERMIT ID: 104 |
| Honeywell - Clearwater Facility | DISTRICT: Southwest |
| ADDRESS: 13350 U.S. Hwy. 19 North | CONTACT PHONE: |
| Clearwater, FL | 727-539-3001 |
| ARMS NO: 1030019 001 | PERMIT NO: | Expiration Date: 2/8/2015 Renewal Date: 12/10/2014 |
|  | 1030019-009-AF |  |
|  |  | Test Due Date: 4/8/2014 |
| EMISSION UNIT DESCRIPTION : Plant 1: Beryllium Operations Consisting of 11 De-burring and 1 Blast Station. Emissions Controlled by a Torit Cyclone Collector Model 20-5, 1500-2500 cfm and Common HEPA Filter Model C-3, GGF2409R type, with 99.997% removal efficiency. |
| INSPECTION DATE: | ARMS INSPECTION TYPE: | COMPLIANCE STATUS: |
|  | March 14, 2013 |  |  | INS1 | ( | INS2 |  | INS3 |  | FUI | ( | IN |  | MNC |  | SNC |
| INSPECTION TYPE: | ( | Initial |  | Re-inspection |  | Complaint |  | Drive-by |  | Quarterly |
| ( | A. General Review: |
| 1. | Permit File Review |  | Yes |  | No |
|  | Comments: |  |  |  |  |
| 2. | Introduction and Entry |  | Yes |  | No |
|  | Comments: |  |  |  |  |
| 3. | Is the Responsible Official/Authorized Representative still: Henry Digdigan? |  | Yes |  | No |
|  | Comments: The Responsible Official/Authorized Representative’s e-mail is: elias.barrios@honeywell.com |
| 4. | Is the facility contact still: Tom Fiedler? |  | Yes |  | No |
|  | Comments: The facility contact’s e-mail is: thomas.j.fiedler@honeywell.com |

| IN | MNC | SNC | B. Specific Conditions: |
| --- | --- | --- | --- |
| ( ( ( ( ( ( ( ( ( ( ( ( ( ( ( ( ( ( ( ( ( ( ( ( ( ( |  |  | Inspection note: This permit is the initial permit for operating as a synthetic minor facility. Previously this was a Title V facility. The permit became effective on 2/9/10 General Conditions [62-4.160, F.A.C.] 12. This permit or a copy thereof shall be kept at the work site of the permitted activity. Comments: A copy of the permit was was not kept at the worksite. 8. If, for any reason, the permittee does not comply with or will be unable to comply with any condition or limitation specified in this permit, the permittee shall immediately provide the Department with the following information: A description of and cause of noncompliance; and The period of noncompliance, including dates and times; or, if not corrected, the anticipated time the noncompliance is expected to continue, and steps being taken to reduce, eliminate, and prevent recurrence of the noncompliance. The permittee shall be responsible for any and all damages which may result and may be subject to enforcement action by the Department for penalties or for revocation of this permit. Comments: Honeywell did not report an episode of noncompliance during the compliance year (1/25/12 – 3/14/13) Common Conditions [Rule 62-296.320(4)(c), F.A.C.] Unless otherwise specified in the permit, the following conditions apply to all emissions units and activities at the facility. Emissions and Controls 2. Circumvention: The permittee shall not circumvent the air pollution control equipment or allow the emission of air pollutants without this equipment operating properly. [Rule 62-210.650, F.A.C.] Comments: There was no circumvention observed in the deburring room, blast station, or the associated duct work. 6. VOC or OS Emissions: No person shall store, pump, handle, process, load, unload or use in any process or installation, volatile organic compounds (VOC) or organic solvents (OS) without applying known and existing vapor emission control devices or systems deemed necessary and ordered by the Department. [Rule 62-296.320(1), F.A.C.] Comments: The deburring room only has touch up small bottles with IPA. These bottles are capped and sealed when not in use. The IPA used to fill the touch up bottles is stored in one gallon containers that are capped and sealed when not in use. This is the only solvent used at this emission unit. 7. Objectionable Odor Prohibited: No person shall cause, suffer, allow or permit the discharge of air pollutants, which cause or contribute to an objectionable odor. An “objectionable odor” means any odor present in the outdoor atmosphere which by itself or in combination with other odors, is or may be harmful or injurious to human health or welfare, which unreasonably interferes with the comfortable use and enjoyment of life or property, or which creates a nuisance. [Rules 62-296.320(2) and 62-210.200(Definitions), F.A.C.] Comments: An upwind/downwind survey of the facility was conducted. The observed parameters were: Downwind odor level detected- None; Wind direction – E/10 mph Upwind odor level detected- None 9. Unconfined Particulate Emissions: No person shall cause, let, permit, suffer or allow the emissions of unconfined particulate matter from any activity, including vehicular movement; transportation of materials; construction, alteration, demolition or wrecking; or industrially related activities such as loading, unloading, storing or handling; without taking reasonable precautions to prevent such emissions. Any permit issued to a facility with emissions of unconfined particulate matter shall specify the reasonable precautions to be taken by that facility to control the emissions of unconfined particulate matter. Reasonable precautions include the following: Paving and maintenance of roads, parking areas and yards. Application of water or chemicals to control emissions from such activities as demolition of buildings, grading roads, construction, and land clearing. Application of asphalt, water, oil, chemicals or other dust suppressants to unpaved roads, yards, open stock piles and similar activities. Removal of particulate matter from roads and other paved areas under the control of the owner or operator of the facility to prevent reentrainment, and from buildings or work areas to prevent particulate from becoming airborne. Landscaping or planting of vegetation. Use of hoods, fans, filters, and similar equipment to contain, capture and/or vent particulate matter. Confining abrasive blasting where possible. Enclosure or covering of conveyor systems. Comments: There were no unconfined emissions observed. Honeywell Corporation maintains the following reasonable precautions: A paved parking lot. Landscaping around the parking lot and plant. Torit cyclone collector that collects beryllium from the deburring room. Administrative Requirements 7 Annual Operating Report: On or before April 1 of each year, the permittee shall submit a completed DEP Form 62-210.900(5), "Annual Operating Report for Air Pollutant Emitting Facility" (AOR) for the preceding calendar year. The report may be submitted electronically in accordance with the instructions received with the AOR package sent by the Department, or a hardcopy may be sent to the Compliance Authority. [Rule 62-210.370(3), F.A.C.] Comments: The latest annual operating report was for calendar year 2011 and was submitted on 2/15/12. 8 Operation Permit Renewal Application: A completed application for renewal of the operation permit shall be submitted to the Permitting Authority with a copy to PCDEM (Compliance Authority) no later than 60 days prior to the expiration date of the operation permit. [Rules 62-4.030, 62-4.050, 62-4.070(3), 62-4.090, 62-210.300(2), and 62-210.900, F.A.C.] Comments: The permit expires on 2/8/15. An application is required to be submitted no later than 12/10/14 A.1. Federal Regulatory Requirements: This emission unit is subject to 40 CFR 61, Subpart C – National Emission Standard for Beryllium, which is adopted by reference in Rule 62-204.800(10), F.A.C. [Rule 62-204.800(10), F.A.C.] Comments: Honeywell meets the provision of this condition during the compliance year. A.2. Permitted Capacity: No more than 12 stations shall be operating simultaneously when processing beryllium. [Rule 62-210.200(PTE), F.A.C.] Comments: During the audit, a review of the daily usage log for the compliance year revealed that at no time were there more than 12 stations operating simultaneously. A.3. Beryllium Emission Standard: The beryllium emissions from the 12 stations at this facility shall not exceed 10 grams over a 24-hour period. [40 CFR 61.32(a) and Rule 62-204.800(10), F.A.C.] Comments: The beryllium emissions did not exceed 10 grams/24 hour period because the maximum number of stations in use at any one time during the compliance year was 5 (10/18/12). A copy of the most recent daily usage log is attached to the inspection report. Additionally, based on the review of the last stack test performed on 2/23/10, the facility produced 0.00085 gr/day of Be emissions compared to the limit of 10 grams/day. This is 99.99% under the limit. During the test, Honeywell had 7 total stations operating. A.4. Compliance Tests: Compliance testing for beryllium emissions from this emission unit shall be conducted during the 105 to 365 day period prior to the expiration date of this permit. The test shall be conducted in accordance with the methods and procedures of 40 CFR 61, Subpart C. Testing of beryllium emissions shall be conducted when the maximum numbers of 12 stations are simultaneously processing beryllium. A compliance test submitted when less than the maximum permitted number of 12 stations are simultaneously processing beryllium will automatically constitute an amended permit to only allow the simultaneous operation of the maximum number of stations that were simultaneously processing beryllium during that test. Once the emission unit is so limited, operation with more stations simultaneously processing beryllium than the most recent compliance test was conducted is allowed for no more than 15 consecutive days for the purpose of additional compliance testing to regain the authority to operate with more stations operating simultaneously processing beryllium than the most recent compliance test, but in no case shall the number of stations simultaneously processing beryllium exceed 12. The test results shall be submitted to the Compliance Authority within 45 days of testing. Acceptance of the test by the Compliance Authority will automatically constitute an amended permit at the higher number of stations tested when simultaneously processing beryllium, but in no case shall the maximum permitted number of 12 stations simultaneously processing beryllium be exceeded. [Rules 62-297.310(2), 62-297.310(7)(a)4.c., 62-297.310(8)(b), and 62-4.070(3), F.A.C.] Comments: The facility must test between 2/8/14 and 12/10/14. A.5. Test Requirements: Tests shall be conducted in accordance with the applicable requirements specified in Appendix D (Common Testing Requirements) of this permit. [Rule 62-297.310(7)(a)9., F.A.C.] Comments: The facility meets the provision of this condition. A.6. Test Method(s): Required tests shall be performed in accordance with the following reference method(s). Method(s) Description of Method and Comments 104 Determination of Beryllium Emissions from Stationary Sources The above method(s) are described in Appendix B of 40 CFR 61 and are adopted by reference in Rule 62-204.800, F.A.C. No other method(s) may be used unless prior written approval is received from the Department. [Rules 62-204.800 and 62-297.100, F.A.C.; and Appendix B of 40 CFR 61] Comments: The facility performed Method 104 only. No other methods were used. The test was performed on 2/23/10. A.7. Test Notification: The permittee shall notify the Compliance Authority in writing at least 15 days prior to any required tests. The notification must include the following information: the date, time, and location of each test; the name and telephone number of the facility’s contact person who will be responsible for coordinating the test; and the name, company, and the telephone number of the person conducting the test. [Rules 62-4.070(3) and 62-297.310(7)(a)9., F.A.C.] Comments: Honeywell notified Air Quality on 1/19/10 and the test was performed on 2/23/10. The notification was received 42 days prior to the Method 104 test. A.8. Test Reports: The permittee shall prepare and submit reports for all required tests in accordance with the requirements specified in Appendix D (Common Testing Requirements) of this permit. The test report shall include: a. A statement indicating the number of stations that were simultaneously processing beryllium during the test period. b. A copy of the daily log as required by Specific Condition No. A.9. for the test day. [Rule 62-297.310(8), F.A.C.] Comments: The Method 104 test results had the following: A statement of the number of stations operating simultaneously A copy of the daily log during the test (Beryllium Permit – Daily Usage Log Plant 1 Beryllium Room). A.9. Recordkeeping Requirements: A daily log for the 1 blast and 11 de-burring stations shall be maintained to document compliance with the limitation of Specific Condition A.2. At a minimum the log shall indicate the following: a. Date, Facility ID, and Emission Unit ID No. (001). b. The number of De-burring and/or Blast Stations in operation. c. Start and stop time for each beryllium operator. d. Facility location (i.e., Plant No. 1). e. Operator name. All records/logs shall be maintained at the facility for at least 3 years and made available to the Department and PCDEM upon request. [Rule 62-4.070(3), F.A.C.] Comments: The facility meets the provisions of the condition. A copy of the latest log is attached to the inspection report. A.10. Operation and Maintenance (O & M) Plan for Torit Cyclone Collector and HEPA Filter Control: The permittee shall comply with the Operation and Maintenance (O&M) Plan for the Torit cyclone collector and HEPA filters, which was submitted with the application dated October 27, 2009. The particulate control devices shall be operated and maintained in accordance with this O&M Plan and as revised with the prior approval of the Compliance Authority (PCDEM). The O&M Plan documentation shall be retained at the facility for at least 2 years and made available to the Department and PCDEM upon request. At a minimum, the O&M Plan shall include the following elements: a. The operating parameters of the respective control device. b. The timetable for the routine maintenance of the control device as specified by the manufacturer. c. The timetable for routine periodic observations of the pollution control device sufficient to ensure proper operation. d. A list of the type and quantity of required spare parts for the control device, which are stored on the premises. e. A record log, which will indicate, at a minimum: 1. When maintenance and observations were performed. 2. What maintenance and observations were performed. 3. Who performed said maintenance and observations. 4. Acceptable parameter ranges for each operational check. [Pinellas County Code, Section 58-128] Comments: A copy of the Beryllium Control Maintenance record is attached to the compliance file. The facility record includes: Lists the frequency of the observation (timetable for routine maintenance). The plant location (where). The description of the part. The procedure and initials of the said maintenance/obs. The record meets the permit condition parameters. C.2. General Pollutant Emission Limiting Standards. Objectionable Odor Prohibited: The permittee shall not cause, suffer, allow or permit the discharge of air pollutants, which cause or contribute to an objectionable odor. An "Objectionable Odor" is defined as any odor present in the outdoor atmosphere, which by itself or in combination with other odors, is or may be harmful or injurious to human health or welfare, which unreasonably interferes with the comfortable use and enjoyment of life or property, or which creates a nuisance [Rules 62-210.200 and 62-296.320(2), F.A.C.; Pinellas County Code, Section 58-178] Comments: Air Quality did not detect any objectionable odors during the inspection. There were no odor complaints during the compliance year. C.3. Circumvention of Control Equipment: The permittee shall not circumvent any air pollution control device or allow the emissions of air pollutants without the applicable air pollution control device [common Torit cyclone collector and common HEPA filter housing control device(s)] operating properly. Increasing the volume of any exhaust stream for the purpose of reducing stack exhaust concentrations is forbidden. This includes allowing dilution air to enter the system through leaks, open vents, or similar means. [Rule 62-210.650, F.A.C.] Comments: Air Quality did not observe circumvention of the Torit cyclone. There is no other control device used at the facility There was no increased volume of the exhaust stream observed during the inspection. Exempt Emission Units/Activities - Cold storage refrigeration equipment – environmental temperature chambers. [Rule 62-210.300(3)(a)5., F.A.C.] - Vacuum pumps in laboratory operations. [Rule 62-210.300(3)(a)6., F.A.C.] - Wood or plastic sanding operations. [Rule 62-210.300(3)(a)8., F.A.C.] - Laboratory equipment – chemical operations and associated fluxes and chemicals. [Rule 62-210.300(3)(a)12., F.A.C.] - Brazing, soldering, or welding operations and associated fluxes and chemicals. [Rule 62-210.300(3)(a)13., F.A.C.] - Emergency electrical generators. [Rule 62-210.300(a)35., F.A.C.; For any engine subject to Title 40, Code of Federal Regulations (CFR), Part 60, Subpart IIII – Standards of Performance for Stationary Compression Ignition Combustion Engines, as long as the permittee operates and maintains the engine according to the manufacturer’s written instructions or procedures over the entire life of the engine and the manufacturer keeps its certification, the engine is not required by the federal rule to demonstrate compliance with emission limits.] - Fire and safety equipments. [Rule 62-210.300(3)(a)15., F.A.C.] - Surface coating facilities with 6.0 gallons or less of coatings per day. [Rule 62-210.300(3)(a)27., F.A.C.] - Degreasing units using heavier-than-air vapors. [Rule 62-210.300(3)(a)23., F.A.C.] - Small diesel holding tanks for emergency generators. [Rule 62-210.300(3)(b)1., F.A.C.] - Diesel fuel transfer to emergency generators. [Rule 62-210.300(3)(b)1., F.A.C.] - Carbon dioxide snow cleaning system – abrasive polishing system. Liquid CO2 is atomized through a nozzle and turns to solid CO2 crystals that physically impinge a part and then turns to gas. [Rule 62-4.040, F.A.C.] - Solvent transfer unloading of 55-gal. drum lots to smaller day containers of less than 10 gal. capacity. Activities with VOC or HAP components are tracked within the materials inventory and mass balance calculations. [Rule 62-4.040, F.A.C.] - Supercritical cleaning using carbon dioxide at its critical point – precision cleaning system. Liquid CO2 is atomized through a nozzle and turns to solid CO2 crystals that physically impinge a part and then turns to gas. [Rule 62-4.040, F.A.C.] - Spray booth 30 psig cleaning using non-regulated solvents. Activities with VOC or HAP components are tracked within the materials inventory and mass balance calculations. [Rule 62-4.040, F.A.C.] - Vacuum/pressure cleaning system. This system uses non-regulated solvents in the process where alternate vacuum and pressure are used to remove all entrapped air in the system. [Rule 62-4.040, F.A.C.] - Vacuum pumps for production environmental chambers. These pumps do not contribute to pollutant activities and only serve to bring environmental test chambers below atmospheric sea-level pressures. Any air pollutants that enter or exit these pumps are already counted in emission calculations. [Rule 62-4.040, F.A.C.] - Bakeout ovens for outer space applications. This is an activity that does not change the emissions as calculated from the mass balance equations. The ovens are allowing complete curing of epoxy systems and removing any residual water from the hardware. [Rule 62-4.040, F.A.C.] - Cold traps on mass transfer systems. Cold traps are used in processes to trap contaminants that might get into high reliability products. These materials are already in the atmosphere and do not cause additional pollution from these activities. [Rule 62-4.040, F.A.C.] - Pressure relief valves. Pressure relief valves act to relieve excessive pressure. They are pollution generating devices and emissions from these devices are captured in overall balance calculations for emissions. [Rule 62-4.040, F.A.C.] - Bulk liquid nitrogen. Liquid nitrogen is used for cooling and is not a listed pollutant. - Shock testing facilities using small quantities of explosives. [Rule 62-4.040, F.A.C.] - Cooling towers. The anti-scaling chemicals used in the cooling towers are included in the chemical inventory. Possible regulated emissions are captured within the material inventory mass balance calculations. [Rule 62-4.040, F.A.C.] - Small electroplating systems – nickel and iron plating system. When plating operations are performed, these activities will follow emission control guidance of the applicable NESHAP – 40 CFR 63, Subpart WWWWWW. [Rule 62-4.040, F.A.C.] - Substitute solvent distillation recovery system – recovers cleaning solvent. Any substitute solvents are tracked for VOC or HAP components within the material inventory and mass balance calculations. [Rule 62-4.040, F.A.C.] - Closed loop washing machines. Solvents used in these systems are tracked for VOC and HAP components within the material inventory and mass balance calculations. [Rule 62-4.040, F.A.C.] - Pick and Place Machine for populating circuit boards. There are no solvent VOCs or HAPs in this process. [Rule 62-4.040, F.A.C.] - Maintenance activities and associated heavy and lubricating oils. [Rule 62-210.300(3)(a)16., F.A.C.] - Custodial activities. [Rule 62-210.300(3)(b)1., F.A.C.] - Hazardous activities – 90-Accumulating & Shipping of RCRA permitted waste. These activities are tracked for VOC or HAP components within the material inventory and mass balance calculations. [Rule 62-4.040, F.A.C.] - Propane used as fuel for lab furnaces, flame deposition, kitchen operations, heat treating operations. Activities with VOC or HAP components are tracked within the material inventory and mass balance calculations. [Rule 62-4.040, F.A.C.] - Water treatment chemicals – Sulfuric acid, Polyelphs (970), Dearcides (735-702), Polymate (910). Activities with VOC or HAP components are tracked within the material inventory and mass balance calculations. [Rule 62-4.040, F.A.C.] - Axarel compounds – high mol. wt., low volatility cleaning solvents. Activities with VOC or HAP components are tracked within the material inventory and mass balance calculations. [Rule 62-4.040, F.A.C.] - Bioact compounds – water soluble cleaners. Activities with VOC or HAP components are tracked within the material inventory and mass balance calculations. [Rule 62-4.040, F.A.C.] - Hollis oils – wave solder heat transfer medium. Activities with VOC or HAP components are tracked within the material inventory and mass balance calculations. [Rule 62-4.040, F.A.C.] |
| ( |  |  | Valid Permit [Rule 62-210.300] |
|  |  |  | Changes to Facility/emission unit [Rule 62-210.300] Does the emission unit description above match what the facility is operating (Number of emission units or points, model number and serial number, etc.) Yes No Comments: |
| ( | C. Other: |
| Pollution Prevention Activities P2 Handouts Provided: P2 Brochure; P2 Manual; P2 Checklist Have any emissions reductions occurred Yes / No Chemical Substitution; Equipment Changes; Process Changes Chemical/Material Reuse; On-site Recycling; Other: Comments: There were no pollution prevention activities during the compliance year. |
| Closing Conference: |
| Inspector(s): Jeffrey Morris, Pinellas County, Air Quality Division |
| Signature(s): Date: | Date: |
| ACCESS? | ( | ARMS? | ( |