| 1030091 88174 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| FACILITY: Morton Plant Mease Healthcare |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PERMIT ID: 322 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DISTRICT: Southwest |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ADDRESS: 1233 South Fort Harrison |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CONTACT PHONE: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Clearwater, FL |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 727-462-7097 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ARMS NO: 1030091 006 |  |  |  |  |  |  |  | PERMIT NO: |  |  |  |  |  |  |  |  |  |  |  | Expiration Date: 1/18/2018 Renewal Date: 11/19/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | 1030091-013-AO |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Test Due Date: 8/1/2000 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| EMISSION UNIT DESCRIPTION : 600 HP Cleaver Brooks, Model CB-600 Steam Boiler fired on natural gas or No. 2 Distillate Fuel Oil, Designated as Boiler No. 006. Maximum heat input rate of 25.3 MMBtu/hour |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| INSPECTION DATE: |  |  |  |  |  |  | ARMS INSPECTION TYPE: |  |  |  |  |  |  |  |  |  |  |  |  |  |  | COMPLIANCE STATUS: |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | November 5, 2013 |  |  |  |  |  |  |  |  | INS1 |  |  | INS2 |  |  | INS3 |  |  | FUI |  |  |  |  |  | IN |  |  | MNC |  |  |  |  |  | SNC |  |
| INSPECTION TYPE: |  |  |  |  | Initial |  |  |  |  |  | Re-inspection |  |  |  |  |  | Complaint |  |  |  |  |  |  | Drive-by |  |  |  |  |  |  | Quarterly |  |  |  |  |
|  |  |  | A. General Review: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1. |  | Permit File Review |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  |  |  | No |
|  |  | Comments: yes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2. |  | Introduction and Entry |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  |  |  | No |
|  |  | Comments: I met with Bob Weber engineer, Mr. Reader had left for the day. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3. |  | Is the Responsible Official/Authorized Representative still: Anthony Reader? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  |  |  | No |
|  |  | Comments: yes The Responsible Official/Authorized Representative’s e-mail is: anthony.reader@baycare.org |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4. |  | Is the facility contact still: Anthony Reader? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  |  |  | No |
|  |  | Comments: yes The facility contact’s e-mail is: anthony.reader@baycare.org |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| IN | MNC | SNC |  |  | B. Specific Conditions: |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ü ü ü ü ü ü ü ü ü ü ü ü ü ü ü ü ü ü ü ü |  |  |  |  | Inspection Note: This permit establishes fuel usage limitations on the facility’s existing boilers and chiller engine to ensure the facility’s potential emissions are below the Title V threshold This permit or a copy thereof shall be kept at the work site of the permitted activity. [General Condition 12.] Comments: The facility had a permit copy posted on bulletin board in Engineer control room available for reference for the plant operators. 3. General Standards – Objectionable Odor: The permittee shall not cause, suffer, allow, or permit the discharge of air pollutants from this facility which cause or contribute to an objectionable odor. Objectionable odor is defined as any odor present in the outdoor atmosphere which by itself or in combination with other odors, is or may be harmful or injurious to human health or welfare, which unreasonably interferes with the comfortable use and enjoyment of life or property, or which creates a nuisance. [Rule 62-296.320(2), F.A.C.; Rule 62-210.200, F.A.C. – Definition of Objectionable Odor; and Pinellas County Code, Section 58-178] Comments: There were no odors detected off the property. 5. General Visible Emissions Standard: Except for emissions units that are subject to a particulate matter or opacity limit set forth or established by rule and reflected by conditions in this permit, no person shall cause, let, permit, suffer or allow to be discharged into the atmosphere the emissions of air pollutants from any activity, the density of which is equal to or greater than 20 percent opacity. EPA Method 9 is the method of compliance pursuant to Chapter 62-297, F.A.C. [Rules 62-296.320(4)(b)1. & 4., F.A.C.] Comments: There were no visible emissions observed the coming from the stacks of the boilers, chiller, generator or any other source at the facility, 6. Test Notification: The permittee shall notify the Air Quality Division of the Pinellas County Department of Environmental Management (PCDEM) at least 15 days prior to the date on which each formal compliance test is to begin of the date, time, and place of each such test, and the test contact person who will be responsible for coordinating and having such test conducted. [Rule 62-297.310(7)(a)9., F.A.C.] Comments: The facility filed notification for testing on 7/17/12 for the 2012 VE test Method 9 performed on 8/2/12 7. Annual Operating Report (AOR): The permittee shall submit to the Air Quality Division of the PCDEM each calendar year on or before March 1, completed DER Form 62-210.900(5), "Annual Operating Report for Air Pollutant Emitting Facility," for the preceding calendar year. The report may be submitted electronically in accordance with the instructions received with the AOR package sent by the Department, or a hardcopy may be submitted. [Rule 62-210.370(3)(a)2., F.A.C.] Comments: The 2012 annual report was received by PCAQ on 4/9/13 and reviewed as acceptable by Bill Froberg. 8. Operation Permit Renewal Application: At least two applications to renew this operating permit shall be submitted to the Air Program of the Southwest District Office of the Department, with an additional copy also sent to the Air Quality Division of the PCDEM no later than 60 days prior to the expiration date of the operation permit… [Rules 62-210.300(2), 62-210.900 and 62-4.070(3), F.A.C.] Comments: This is not applicable at this time the renewal date is 11/19/2017 and the permit does not expire until 1/18/2018 - Specific Conditions for EU Nos. 005 and 006 – Steam Boilers 1 and 2 A1. Federal Regulatory Requirements - Both boilers (EU Nos. 005 and 006) are subject to and must meet the applicable requirements of 40 CFR 60 - Standard of Performance for New Stationary Sources (NSPS), Subpart Dc - Standards of Performance for Small Industrial-Commercial-Institutional Steam Generating Units, 40 CFR 60.40c through 60.48c. The applicable NSPS requirements have been incorporated into this permit (see Specific Condition Nos. A.2.a., A.10., A.12., A.13., and A.15.) [Rule 62-204.800(8)(b), F.A.C.; NSPS 40 CFR 60 Subpart Dc] Comments: The facility is complying with this rule in regards to these emission units for meeting their fuel usage limitation, sulfur content limitation, records keeping for the rolling 12 monthly total was up to date, and only semiannual reporting of sulfur content is required. A2. Fuel Limitations - Each boiler is permitted to fire on natural gas or new (virgin) No. 2 distillate fuel oil with the following restrictions: - The sulfur content of the No. 2 fuel shall not exceed 0.05% S (50 ppm) by weight*; (* NSPS Subpart Dc Note - The sulfur content limitation of this BACT Determination is more stringent than, and therefore meets the requirements of, 40 CFR 60 Subpart Dc 0.5 weight percent sulfur standard for sulfur dioxide contained in 40 CFR 60.42c(d).) - No. 2 fuel oil usage for both boilers combined is limited to a total of 1,974,500 gallons in any consecutive 12-month period**; (** Permitting Note – The above fuel oil usage limitation assures that potential emissions from this facility will remain below Title V major source levels.) - waste or recycled oil is not permitted to be used; and - the monthly average maximum heat input rate for each boiler shall not exceed 25.3 MMBtu/hour when fired on No. 2 fuel oil, or 25.1 MMBtu/hour (monthly average) when fired on natural gas. [Rules 62-210.200, (Definition of Potential to Emit), and 62-296.406, F.A.C.); Best Available Control Technology (BACT) Determination dated 2/28/1996 (see Appendix E); Construction Permit 1030091-012-AC;] Comments: The facility uses natural gas for most of its operations. This is the more economical fuel. The record logs showed the alternating of boilers on a monthly bases and use of natural gas. The boiler number one was fired on fuel oil in July and November 2012 for the yearly maintenance, total usage of 20 and 67 gallons for 1 and 3 hours. The combined usage of fuel oil for both boilers for the 12month period was 275 hours. There has been no fuel oil usage in boiler two for 2013 to this date. (See records) A.4.. Visible Emissions: Visible emissions (VE) from each boiler stack shall not exceed 20% opacity, except for one two-minute period per hour during which opacity shall not exceed 40%. [Rule 62-296.406(1), F.A.C.] Comments: The boilers were tested and resulted in 0% opacity, during testing 8/2/12 during a permit renewal. The annual test for 2013 was waived based on less than 400 hour of fuel oil usage. A.5. Compliance Tests - During each federal fiscal year (October 1st to September 30th), each boiler shall be tested to demonstrate compliance with the visible emissions (VE) standard of Specific Condition No. A.4., unless the test is waived (see Specific Condition No. A.6.). [Rule 62-297.310(7)(a), F.A.C.] Comments: The 2013 annual test was waived based on less than 400 hours of fuel usage for boilers in the past 12 month periods. A.6.. VE Compliance Test Waiver - Each federal fiscal year visible emissions compliance tests can be waived for either or both boilers, on a year by year basis if fuel oil has not been used in the boiler for more than 400 hours for the previous 12 months and if it is not expected to be used in the boiler for more than 400 hours during the next 12 months, except that, regardless of fuel used, a VE test shall be conducted on each boiler between 120 days and 180 days prior to applying for renewal of the facility’s operation permit. This prior-to-permit renewal compliance test may be done while firing natural gas if the < 400 hour of oil firing requirement above has been met. Each year when the VE test is due, if this test waiver provision is invoked, a letter must be sent to the Compliance Authority (Pinellas County Air Quality Division) stating that the above requirements for the waiver have been satisfied. This notification letter shall include a statement, for each boiler, of the number of hours that fuel oil was fired during the last 12 month period, and, if fuel oil was fired for any period during the last 12 months, a copy of the most recent fuel records that document compliance with the % sulfur content limit in accordance with Specific Condition No. A.2.a. [Rules 62-297.310(7)(a)3. and 5., F.A.C.; Construction Permit 1030091-012-AC] Comments: The VE test was waived for 2013. The facility submitted letter June 3, 2013 with record logs Fuel sulfur content 15 ppm invoice. The letter stated 3 hours of fuel oil operation with no plans to exceed 400 hours limitation during the next 12 month period . Review of 2012 - 2013 records, during inspection shows the boilers operations highest monthly rolling 12 month record total was 275 hours. A.7. Compliance Test Method - Required visible emissions (VE) compliance tests shall be performed in accordance with the following reference method. DEP Method; Description of Method and Comments. 9; Visual Determination of the Opacity of Emissions from Stationary Sources - The visible emissions test shall be conducted by a certified observer (see Rule 62-297.320, F.A.C.), and be a minimum of sixty (60) minutes in duration. The visible emissions test observation period shall include the period during which the highest opacity emissions can reasonably be expected to occur (see Specific Condition No. A.9.). The minimum requirements for stationary point source emission test procedures and reporting shall be in accordance with Chapter 62-297, F.A.C. and 40 CFR 60 Appendix A. The above DEP Method 9 is described in Rule 62-297.401(9)(c), F.A.C., which also adopts and references EPA Method 9. EPA Method 9 is described in Appendix A of 40 CFR 60 and adopted by reference in Rule 62-204.800, F.A.C. No other method(s) may be used unless prior written approval is received from the Department. [Rules 62-204.800, 62-297.320, and 62-297.401(9)(c), F.A.C.; and Appendix A of 40 CFR 60] Comments: Method 9 required for the facility The boilers were tested and resulted in 0% opacity, during testing 8/2/12. No test required for 2013. A.Q. staff performed a method 9 today on boiler #2 during moderate fire rate. The resulting opacity was 0% . (see test attached) A8. Compliance Test Requirements - Compliance tests shall be conducted in accordance with the applicable requirements specified in Appendix D (Common Testing Requirements) of this permit. [Rule 62-297.310, F.A.C.] Comments: The facility met the Appendix D requirements during the 2012 test performance. The annual Test was waived for 2013. A.9. Operating Rate During Testing – Visible emissions (VE) compliance tests shall be conducted during operation of the boiler within 90-100% of the maximum permitted fuel heat input rate (see Specific Condition No. A.2.d.), when feasible. VE tests shall be conducted while firing fuel oil, except that natural gas may be fired during the prior-to-permit renewal compliance test if the fuel oil firing operating hour limitations are met (see Specific Condition No. A.6.). A compliance test submitted for operation while firing fuel oil at a fuel oil firing heat input rate less than 90% of the maximum permitted rate will automatically constitute an amended permitted fuel oil heat input rate at that lesser rate plus 10%. Once the unit is so limited, operation at higher capacities while firing fuel oil is allowed for no more than 15 consecutive days for the purpose of additional compliance testing to regain the authority to operate at the permitted capacity. The test results shall be submitted to the Compliance Authority (Pinellas County Air Quality Division) within 45 days of testing. Acceptance of the test by the Compliance Authority will automatically constitute an amended permit at the higher tested heat input rate plus 10%, but in no case shall the maximum permitted heat input rate specified in Specific Condition No. A.2.d. be exceeded. The fuel type and heat input rate (MMBtu/hour) during the test shall be included with each test report. Failure to submit the required fuel information or operating under conditions that are not representative of normal operating conditions may invalidate the test and fail to provide reasonable assurance. [Rule 62-4.070(3), F.A.C.; Construction Permit 1030091-012-AC] Comments: The test was performed 8/2/12 at 11.6 MMbtu during operation high fire on natural gas, this does not exceed the Maximum heat input rate of 25.3 MMBtu/hour. . The test was performed on 8/2/12 and received 8/8/12 within 45 days of testing. A.10. Fuel Oil Sulfur Content Documentation During VE Compliance Test - Compliance with the fuel oil sulfur content requirements of Specific Condition No. A.2.a. shall be demonstrated during any VE test conducted while burning fuel oil, by submitting any of the following with the VE test report: a. copy of a fuel oil analysis from the fuel oil supplier, or a vendor shipment receipt showing delivery of low sulfur oil containing a maximum of 0.05% (or 50 ppm) sulfur by weight, representative of the oil used during the compliance test; or b. results of the fuel oil analysis for an as-burned fuel oil sample taken during the compliance test. Fuel sampling and analysis shall be in accordance with 40 CFR 60 Appendix A, Method 19, Section 5.2.2 (Liquid Fossil Fuel). [Rules 62-4.070(3) and 62-204.800, F.A.C.; NSPS Subpart Dc 40 CFR 60.44c(g) & (h)] Comments: The FDEP office Air engineer Cindy Zhang Torres sent correspondence 8/2/12 to the A.Q. Program Coordinator Gary Robbins stating the VE testing for the boilers could be performed while firing on natural gas..The boilers each of fuel oil #2 demonstrated the fuel oil usage was below 400 hours for the 12 month periods in 2012 and 2013. (See record log) The annual compliance test for 2013 was granted a waiver on June 12/2013 (See AQ letter in file) A.11. Compliance Test Notification - The permittee shall notify the Compliance Authority (Pinellas County Air Quality Division) in writing at least 15 days prior to any required compliance tests. The notification must include the following information: the date, time, and location of each test; the name and telephone number of the facility’s contact person who will be responsible for coordinating the test; and the name, company, and the telephone number of the person conducting the test*. (* Permitting Note - The notification should also include the relevant emission unit ID No(s)., test method(s) to be used, and pollutants to be tested.) [Rules 62-4.070(3) and 62-297.310(7)(a)9., F.A.C.] Comments: The facility filed notification for testing on 7/17/12 for this 2012 VE test on Method 9, and performed on 8/2/12. The method 9 for 2013 was not performed received waiver because the fuel oil usage was below 400 hours for the 12 month period. A.12.. Fuel Type and Usage Records: In order to document compliance with the requirements of Specific Condition Nos. A2., A.6., and A.9., the permittee shall maintain monthly records of No. 2 distillate fuel oil and natural gas used in each boiler. The records shall include the following: Monthly Records: - Facility ID, Emission Unit ID No. and Description; - Month and Year; - Monthly total operating hours of each boiler when burning No. 2 fuel oil; - Monthly total operating hours of each boiler when burning natural gas; - 12-month rolling total operating hours of each boiler when burning No. 2 fuel oil; - Monthly total quantity of No. 2 fuel oil burned by each boiler; - Monthly total quantity of natural gas burned by each boiler; - Monthly average heat input of each boiler fired on natural gas in MMBtu/hr; - Monthly average heat input of each boiler fired on No. 2 fuel oil in MMBtu/hr; and - 12-month rolling total quantity of fuel oil burned by both boilers. Daily records shall be completed within three (3) business days. Monthly records shall be completed by the end of the following month. These records shall be maintained for a minimum of the most recent three (3) year period and made available to the Department and the PCDEM upon request. [Rules 62-4.070(3) and 62-204.800, F.A.C.; 40 CFR 60.48c(g) & 60.48c(i)] Comments: The records meet all of the conditions listed under A12 for (1-10.) (See 2012-2013 attached copy of records). A.13. Fuel Oil Sulfur Content Records: Ongoing compliance with the fuel oil sulfur content requirements of Specific Condition No. A2 shall be demonstrated through fuel oil analysis provided by the fuel supplier or fuel sampling of each shipment of oil delivered for use in these boilers. The fuel oil analysis provided by the fuel supplier shall consist of: - The name of the supplier. - The sulfur content in fuel oil, and the American Society for Testing and Materials (ASTM) method used to determine the sulfur content in fuel oil. ASTM D5453-06 Standard Test Method for Determination of Total Sulfur in Light Hydrocarbons, spark Ignition Engine Fuel, Diesel Engine Fuel and Engine Oil by Ultraviolet Florescence, or other ASTM methods approved by the Department shall be used to analyze the fuel oil. If fuel sampling is used to demonstrate compliance, the fuel sampling and analysis shall be performed in accordance with 40 CFR 60 Appendix A, Method 19. - A statement from the oil supplier that the oil complies with the specifications under the definition of distillate oil in §60.41c. These records shall be recorded in a permanent form suitable for inspection upon request, and shall be retained for at least a two (2) year period. [Rules 62-4.070(3), 40 CFR 60.48c(f), and 62-204.800, F.A.C.] Comments: The analysis is for McMullen Oil Company forNA1993 Dyed Diesel fuel oil No 2 with 15 ppm sulfur. (See copy attached ) A.14. Compliance Test Reports - The permittee shall prepare and submit reports for all required compliance tests in accordance with the requirements specified in Appendix D (Common Testing Requirements) of this permit. The fuel type and heat input rate (MMBtu/hour) during the test shall be included with each test report. [Rule 62-297.310(8), F.A.C.] Comments: The Method 9test performed in 2012 with a heat input rate of 11.6 MMbtu during operation high fire on natural gas, since fuel oil requirement had been waived by FDEP. A.15.. Semi-Annual Fuel Sulfur Content Reports - The permittee shall submit semi-annual reports of fuel oil sulfur content records required in Specific Condition No. A.13. to the Compliance Authority (Pinellas County Air Quality Division) postmarked by the 30th day following the end of the reporting period (i.e., January – June report postmarked by July 30 and July – December report postmarked by January 30 of each year). Each semi-annual report shall include a certified statement signed by the owner or operator of the facility that the record submitted represents all of the fuel combusted during the six-month period covered by the report. No semi-annual report is required if no oil was combusted or delivered during the 6-month period being reported. [Rule 62-204.800(8), F.A.C.; NSPS Subpart Dc 40 CFR 60.48c(j)] Comments: The Semi annual Report was submitted on July 12, 2013 for the Jan 1, 2013 – June 30th 2013 with records and fuel McMullen Oil Company forNA1993 Dyed Diesel fuel oil No 2 15 ppm sulfur. (See file copy ) |
| ü |  |  |  |  | #### Valid Permit [Rule 62-210.300] |  |  |  |  |  |
| ü |  |  |  |  | #### Changes to Facility/emission unit [Rule 62-210.300] Does the emission unit description above match what the facility is operating (Number of emission units or points, model number and serial number, etc.) Yes No Comments: No changes |  |  |  |  |  |
| ü |  |  | C. Other: |  |  |  |  |  |  |  |
| Pollution Prevention Activities - P2 Handouts Provided: P2 Brochure; P2 Manual; P2 Checklist - Have any emissions reductions occurred Yes / No Chemical Substitution; Equipment Changes; Process Changes Chemical/Material Reuse; On-site Recycling; Other: Comments: No changes |  |  |  |  |  |  |  |  |  |  |
| Closing Conference: I informed Mr. Weber , the facility appears to be in compliance. I suggested the facility could send in an administrative correction letter if they need to add addition of his name as facility contact. I told him if they need to send in a change for the facility responsible official they would need to file an amendment to the permit. |  |  |  |  |  |  |  |  |  |  |
| Inspector(s): Shea Jackson, Pinellas County, Air Quality Division |  |  |  |  |  |  |  |  |  |  |
| Signature(s): Date: |  |  |  |  |  |  |  |  | Date: November 7, 2013 |  |
| # ACCESS? |  |  |  | ü |  | # ARMS? | ü |  |  |  |

Morton Plant Mease Healthcare

1233 South Fort Harrison, Clearwater

Project Id:	88174	Permit No: 1030091-013-AO	Arms Number: 0091 006

Inspector:	Shea Jackson	Inspection Date / Time: 11/5/2013  / _______

Source (EU):	600 HP Cleaver Brooks, Model CB-600 Steam Boiler fired on natural gas or No. 2 Distillate Fuel Oil, Designated as emission unit No.006. Maximum heat input rate of 25.3 MMBtu/hour

Description:	[The south boiler on the left is the number 2 boiler operating at moderate load].

Morton Plant Mease Healthcare

1233 South Fort Harrison, Clearwater

Project Id:	88174	Permit No: 1030091-013-AO	Arms Number: 0091 006

Inspector:	Shea Jackson	Inspection Date / Time: 11/5/2013  / _______

Source (EU):	600 HP Cleaver Brooks, Model CB-600 Steam Boiler fired on natural gas or No. 2 Distillate Fuel Oil, Designated as emission unit No.006. Maximum heat input rate of 25.3 MMBtu/hour

Description:	[Southern most stack of two is the Number 2 boiler, and was in operation at this time.  No visible emission only heat waves].