1030153 003 66922

| FACILITY: HOWCO Environmental Services, Inc. | PERMIT ID: 1545 |
| --- | --- |
|  | DISTRICT: Southwest |
| ADDRESS: 843 43rd Street South | CONTACT PHONE: |
| St. Petersburg, FL | 727-328-7403 |
| ARMS NO: 1030153 003 | PERMIT NO: | Expiration Date: 1/31/11 Renewal Date: 12/2/10 |
|  | 1030153-009-AO & 1030153-008-AC |  |
|  |  | Test Due Date: |
| EMISSION UNIT DESCRIPTION : Oil Recycling Operation: One Oil Heater (Hy-Way Vertical Helical Coil Thermal Fluid Heater, Model MKVO-600), Two Heated Oil Tanks, a Condesing Unit, and a Flash Tower. The oil heater is fired on virgin No. 2 fuel oil with a maximum sulfur content of 0.5% |
| INSPECTION DATE: | ARMS INSPECTION TYPE: | COMPLIANCE STATUS: |
|  | November 18, 2008 |  |  | INS1 |  | INS2 |  | INS3 |  | FUI |  | IN |  | MNC |  | SNC |
| INSPECTION TYPE: |  | Initial |  | Re-inspection |  | Complaint |  | Drive-by |  | Quarterly |
| ( | A. General Review: |
| 1. | Permit File Review |  | Yes |  | No |
|  | Comments: |  |  |  |  |
| 2. | Introduction and Entry |  | Yes |  | No |
|  | Comments: |  |  |  |  |
| 3. | Is the Responsible Official/Authorized Representative still: Tim Hagan? |  | Yes |  | No |
|  | Comments: |
| 4. | Is the facility contact still: Richard Dillen cel.ph. 727-385-1242? |  | Yes |  | No |
|  | Comments: |

| IN | MNC | SNC | B. Specific Conditions: |
| --- | --- | --- | --- |
|  |  |  | Inspection Note: The facility is currently operating under two permits (1030153-008-AC and 1030153-009-AO. Both have an effective date of 04/13/2006. 1030153-008-AC allows for an increase in hours of operation for air stripper 2 from 4450 to 8760/year, without increasing emissions This permit or a copy thereof shall be kept at the work site of the permitted activity. [62-4.160 F.A.C. - General Condition 12.] Comments: The facility did did not have a copy of the permit on-site. 3. General Visible Emissions (VE) Limit – Visible emissions from this facility shall be less than 20% opacity. [Rule 62-296.320(4)(b)a, F.A.C.] 28. Visible Emission (VE) Testing - The oil heater's exhaust stack shall be tested for visible emissions during 12 month period prior to the expiration date (09/28/2010) of this permit but no later than July 28, 2005. Copies of the test data shall be submitted to the Air Compliance Section of this office and the PCDEM within 45 days of the testing in conjunction with the application to renew this permit. (See Specific Condition Nos. 30.A, 30.B, 31., 32 and 33 for additional information to be submitted as part of the test report.) [Rules 62-297.310(7)(a) and 62-297.310(8)(b), F.A.C.] 29. VE Test Methods - Compliance with the visible emission limitation of Specific Condition No. 26 shall be determined using EPA Method 9 and shall be conducted by a certified observer and be a minimum of thirty (30) minutes in duration. The test observation period shall include the period during which the highest opacity emissions can reasonably be expected to occur. The minimum requirements for stack sampling facilities, source sampling and reporting, shall be in accordance with 40 CFR 60, Appendix A, and adopted by reference in Chapter 62-297, F.A.C. [Rules 296.310(2)(c) and 62-297.310(4)(a)2., F.A.C.] Comments: I did not perform a Method 9 VE, but as I arrived and while I was in the Lab across the street from the burner, I was able to see it through the window and there were no emission emanating from its stacks. 4. Circumvention – The permittee shall not allow any person to circumvent any pollution control device or allow the emissions of air pollution without the applicable air pollution control device operating properly. [Rule 62-210.650, F.A.C.] Comments: This EU does not have control devices associated with it. 5. Fugitive VOC/Organic Solvents (OS) – The permittee shall not store, pump, handle, process, load, unload, or use in any process or installation, volatile organic compounds (VOC), Hazardous Air Pollutants (HAPs), or organic solvents without applying known and existing vapor emission control devices or systems deemed necessary and ordered by the Department. The following procedures shall be utilized to minimize pollutant emissions: maintain tightly fitting cover, lids, etc. on all containers of OS/VOC/HAPs when they are not being handled, tapped, etc.; all VOC/HAPs fittings, valve lines, etc. shall be properly maintained; all VOC/HAPs spills shall be attended to immediately and the waste properly disposed of, recycled, etc.; all solvent from solvent washings (equipment clean-up) shall be directed into containers that prevent evaporation to the atmosphere; and prevent excessive air turbulence across exposed VOC/OS. [Rule 62-296.320(1), F.A.C.] Comments: All hoses, pipes, valves and fittings were being properly maintained such that leaks and spills were kept to a minimum. 6. Objectionable Odor - The permittee shall not cause, suffer, allow or permit the discharge of air pollutants, which cause or contribute to an objectionable odor. An objectionable odor is any odor present in the outdoor atmosphere which by itself or in combination with other odors, is or may be harmful or injurious to human health or welfare, which unreasonably interferes with the comfortable use and enjoyment of life or property, or which creates a nuisance. [Rules 62-296.320(2) and 62-210.200(181), F.A.C; Pinellas County Code, Section 58-178] Comments: There were no odors outside of the property boundaries which could he attributed to Howco. 7. Special Compliance Tests - When the Department and/or the Pinellas County Department of Environmental Management (PCDEM), after investigation, have good reason (such as complaints, increased visible emissions or questionable maintenance of control equipment) to believe that any applicable emission standard contained in a Department rule or in a permit issued pursuant to those rules is being violated, it shall require the owner or operator of the emissions unit to conduct compliance tests which identify the nature and quantity of pollutant emissions from the emissions unit and to provide a report on the results of said tests to the Department and the PCDEM. [Rule 62-297.310(7)(b), F.A.C.] Comments: No tests have been ordered or deemed necessary. 8. Testing Notification - The permittee shall notify the Air Compliance Section of the PCDEM at least 15 days prior to the date on which each formal compliance test is to begin of the date, time and place of each such test, and the test contact person who will be responsible for coordinating and having such test conducted. [Rule 62-297.310(7)(a) 9., F.A.C.] Comments: The facility provided the AQD with notification of testing more than 15 days advance notice. 9. Recordkeeping: Retention – All records required by this permit shall be maintained at the facility in a form suitable for inspection for at least five (5) years and be made available to the PCDEM and Department upon request. [Rule 62-4.070(3) F.A.C.] Comments: HOWCO has records going back to 2003. 10. Recordkeeping: Frequency - Daily records shall be completed within 3 business days and monthly records shall be completed by the end of the following month. [Rule 62-4.070(3), F.A.C.] Comments: Daily records were completed within 3 business days and monthly records by the end of the following month. 11. Modification – Any proposed change to this source which will cause the limitations of this permit to be exceeded, such as design parameters, may be considered a modification and must be reported to this office and the PCDEM prior to implementing the change for proper processing. [Rule 62-4.070(3), F.A.C.] Comments: There have been no materials or process changes per MA Richard Dillen and none that I could see. 12. Annual Operating Report – Submit to the Air Compliance Sections of this office and the PCDEM (unless otherwise directed by the Department) for this facility, each calendar year and on or before March 1, an annual operating report [DEP Form 62-210.900(5)] for the preceding calendar year pursuant to Rule 62-210.370(3), F.A.C. [Rule 62-210.370(3), F.A.C.] Comments: Howco submitted the 2007 AOR on February 20th, 2008. 24. Fuel Type - The oil heater is permitted to burn only the following fuels: Virgin No. 2 fuel oil with a maximum sulfur content of 0.5% by weight. B. "On-Specification" (see Specific Condition No. 25) used No. 5 fuel oil with a maximum sulfur content of 0.75% by weight. [Rule 62-4.070(3), F.A.C. and Construction Permit No. 1030153-008-AC] Comments: HOWCO was using and continues to On-Spec No.5 used Oil with the highest rate of usage in October 2008 at 32.67 gallons per hour. 25. Fuel Flow Rate - The fuel oil firing rate for this oil heater shall not exceed 34.5 gallons per hour (corresponds to approximately 4.8 MMBtu/hr). [Construction Permit No. 1030153-008-AC] Comments: HOWCO was using and continues to On-Spec No.5 used Oil with the highest rate of usage in October 2008 at 32.67 gallons per hour. 26. Visible Emissions - Visible emissions from the oil heater's stack shall not be equal to or greater than 20% opacity. [Rule 62-296.320(4)(b), F.A.C.] Comments: I did not perform a Method 9 VE, but as I arrived and while I was in the Lab across the street from the burner, I was able to see it through the window and there were no emission emanating from its stacks. 27. Reclaimed (Used) Fuel Oil Specification - The permittee shall not burn off-specification used oil. For each delivery of on-specification used oil, the vendor shall provide a Certificate of Analysis* documenting the fuel oil meets the following requirements of 40 CFR 761.20(e)(2) and (3) and 40 CFR 279.11 (July 1, 2001): Constituent/Property Allowable Level Arsenic 5 ppm maximum Cadmium 2 ppm maximum Chromium 10 ppm maximum Lead 100 ppm maximum Total Halogens Shall not exceed 1000 ppm1 Flash Point 100 degrees F minimum PCB’s Shall be less than 2 ppm2 1Levels over 1000 ppm require additional testing (ref. 40 CFR 279.11) 2Required to be capable of firing on-specification used oil during startup and shutdown. Firing of 2 ppm or greater PCB containing used oil is prohibited. *Copies of the Certificate of Analysis shall be maintained at the facility for a minimum of 5 years and made available to the Department and/or the Approved Local Air Program Office (if applicable) upon request. [Rules 62-4.070(3) and 62-710.210 F.A.C.] Comments: Allowable Level Actual Level COA Arsenic 5 ppm maximum < 1.0 ppm Cadmium 2 ppm maximum < 2.0 ppm Chromium 10 ppm maximum < 5.0 ppm Lead 100 ppm maximum < 100 ppm Total Halogens Shall not exceed 1000 ppm1 562 ppm Flash Point 100 degrees F minimum > 140 deg F PCB’s Shall be less than 2 ppm2 < 2 ppm 30. Operation During Testing – The oil recycling operation shall comply with the following: A. Testing shall be conducted while firing No. 5 "on-specification" used oil unless used oil has been fired in the oil heater for less than 400 hours during the previous consecutive12-month period. In that case the test may be conducted while firing new No. 2 fuel oil. If the most recent test was conducted when firing new No. 2 fuel oil, then within 30 days of exceeding the 400th hour of firing No. 5 "on-specification" used oil a new test shall be conducted when firing used oil. A statement of the type of oil fired during the test, with a fuel oil certification, shall be included with all test reports B. Testing of emissions shall be conducted during firing of the oil heater at permitted capacity (defined as a fuel firing rate within 90-100% of the maximum permitted fuel firing rate of 34.5 gallons/hour (4.8 MMBtu/hour)). If it is impractical to test at permitted capacity, a compliance test may be conducted at a lower rate. Subsequent unit operation is limited to 110% of the tested rate until a new test is conducted. Once the unit is so limited, operation at higher fuel firing rates is allowed for no more than 15 consecutive days for purposes of additional compliance testing. The test results shall be submitted to the Air Compliance Section of this office and the PCDEM within 45 days of testing. Acceptance of the test by the Department will automatically constitute an amended permit at the higher tested rate plus 10%, but in no case shall the maximum permitted fuel oil firing rate of 34.5 gallons/hour be exceeded. A statement of the oil firing rate during the test shall be included with all test reports. Failure to submit the process rate or operating under conditions that are not representative of normal operating conditions may invalidate the test and fail to provide reasonable assurance. [Rules 62-297.310(7)(a)4, 62-297.310(8) and Rule 62-297.310(2), F.A.C.] Comments: testing was performed while firing On-Spec Used Oil No. 5. 31. Test Report – The following shall be submitted with any compliance test report: A. Type of fuel oil used in the oil heater and oil flow rate (gallons/hour). B. Fuel oil analysis for the sulfur content. (virgin No. 2 fuel oil and “on-specification” used No. 5 fuel oil, as used). C. “On-specification” used No. 5 fuel oil analysis to document compliance with the “on-specification” used oil limits. D. A copy of the emission test records for the month the test was conducted as required by Specific Condition No. 28. [Rule 62-4.070(3), F.A.C. and Construction Permit No. 1030153-008-AC] Comments: The EU was in compliance with A, B, C and D above. 32. Operating Records – In order to document compliance with the requirements of Specific Condition Nos. 25 and 27, the permittee shall keep the following operation records: Daily Records type of fuel oil used in the oil heater; oil heater operating hours; oil heater fuel usage (gallons) average fuel oil firing rate for the oil heater (gallons per hour) based on B. and C. above. In addition, “On-specification” used No. 5 fuel oil analysis reports (i.e., copies of the Certificate of Analysis) for each delivery of on-specification used oil shall be maintained at the facility for a minimum of 5 years and made available to the Department and/or the Approved Local Air Program Office (if applicable) upon request. [Rule 62-4.070(3), F.A. C. and Construction Permit No. 1030153-008-AC] Comments: The facility was in compliance with the recordkeeping requirements for EU 003above. 33. Fuel Oil Sulfur Content Documentation - In order to document continuing compliance with the sulfur content limitations of Specific Condition No. 24, in % by weight, of the fuel oil used in the oil heater, the permittee shall keep records on either vendor provided as-shipped analysis or on analysis of as-received samples taken at the plant. The analysis shall be determined by ASTM methods ASTM D4057-88 and ASTM D129-91, ASTM D2622-94 or ASTM D4294-90, adopted and incorporated by reference in Rule 62-297.440(1), F.A.C. [Rule 62-4.070(3), F.A.C.] Comments: The On-Spec Used Oil No. 5 Sulfur content was 0.10 % per the COA attached. There were no exceedences of Sulfur content throughout the year. 34. Air Operating Permit Renewal Application – A completed application for an air operating permit shall be submitted to the Air Program of the Department’s Southwest District Office along with a copy to the PCDEM, no later than 60 days prior to the expiration date of the operation permit…. [Rules 62-4.050, 62-4.070(3), 62-4.090, 62-210.300(2), and 62-210.900, F.A.C.] Comments: I read the permit condition to Mr. Dillen. |
|  |  |  | Valid Permit [Rule 62-210.300] |
|  |  |  | Changes to Facility/emission unit [Rule 62-210.300] Does the emission unit description above match what the facility is operating (Number of emission units Yes No Comments: |
| ( | C. Other: |
| Pollution Prevention Activities P2 Handouts Provided: P2 Brochure; P2 Manual; P2 Checklist Have any emissions reductions occurred Yes / No Chemical Substitution; Equipment Changes; Process Changes Chemical/Material Reuse; On-site Recycling; Other: Comments: There were no chemical or physical equipment changes per Mr. Dillen and none that I could see. |
| Closing Conference: EU 003 was in compliance for gallons of On Spec Used Oil burned per hour and Informed Mr. Dillen that Howco was in compliance. |
| Inspector(s): Jose Rodriguez, Pinellas County, Air Quality Division |
| Signature(s): Date: | Date: November 19, 2008 |
| ACCESS? |  | EASIIR? |  |

H:\users\wpdocs\airqual\Air_Compliance\AQI\1030153 003 66922.doc