1030153 004 71064

| FACILITY: HOWCO Environmental Services, Inc. | PERMIT ID: 2245 |
| --- | --- |
|  | DISTRICT: Southwest |
| ADDRESS: 843 43rd Street South | CONTACT PHONE: |
| St. Petersburg, FL | 727-437-4059 |
| ARMS NO: 1030153 004 | PERMIT NO: | Expiration Date: 1/31/11 Renewal Date: 12/2/10 |
|  | 1030153-011-AO & 1030153-010-AC |  |
|  |  | Test Due Date: 5/30/00 |
| EMISSION UNIT DESCRIPTION : Air Stripper No. 2 - Environmental Products, Inc. Shallow Tray Model No. 3631 |
| INSPECTION DATE: | ARMS INSPECTION TYPE: | COMPLIANCE STATUS: |
|  | 23 March 2010 |  |  | INS1 | ( | INS2 |  | INS3 |  | FUI | ( | IN |  | MNC |  | SNC |
| INSPECTION TYPE: | ( | Initial |  | Re-inspection |  | Complaint |  | Drive-by |  | Quarterly |
| ( | A. General Review: |
| 1. | Permit File Review |  | Yes |  | No |
|  | Comments: |  |  |  |  |
| 2. | Introduction and Entry |  | Yes |  | No |
|  | Comments: Mr. Richard Dillen answered my question and provided the VOC logs, Certificates of Analysis etc and gave me a tour of the facility. |  |  |  |  |
| 3. | Is the Responsible Official/Authorized Representative still: Tim Hagan? |  | Yes |  | No |
|  | Comments: The Responsible Official/Authorized Representative’s e-mail is: |
| 4. | Is the facility contact still: Richard Dillen? |  | Yes |  | No |
|  | Comments: The facility contact’s e-mail is: rdillen@howcousa.com |

| IN | MNC | SNC | B. Specific Conditions: |
| --- | --- | --- | --- |
|  |  |  | Inspection note: These permits were issue simultaneously to: - allow the oil heater to burn reclaimed (used) fuel oil that has a flash point below 100 degrees F; - add a work practice requirement regarding the procedure to re-direct an oil heater’s thermal oil coming from the burner to the correct processing oil tanks (cookers); - change the retention of records at the facility from 5 years to 3 years; - clarify that the visible emissions test report of the oil heater’s stack is not required to be submitted with the air permit renewal application, but does need to be submitted within 45 days of testing; - require the visible emissions test of the oil heater’s stack is to be conducted at least 105 days prior to and no more than 365 days prior to the date of January 31, 2011 (the expiration date of the facility’s current operation permit), instead of during the 12 month period prior to January 31, 2011; - require one recent month of records be submitted with a permit renewal application, instead of two; - require fuel oil used in the oil heater to be analyzed with the appropriate ASTM method or EPA approved methods, instead of using out-dated ASTM methods. - clarify the oil heater’s max allowable fuel oil usage rate of 34.5 gal/hr is based on a daily average. - Added a daily recordkeeping requirement (Specific Condition No. C.12.) to document the hours the oil heater burns reclaimed fuel oil if the last visible emission test was conducted when burning new No. 2 fuel oil in order to determine when a new visible emission test burning reclaimed fuel oil is required. General Conditions [62-4.160, F.A.C.] 12. This permit or a copy thereof shall be kept at the work site of the permitted activity. Comments: A copy of the permit was was not kept at the worksite. 8. If, for any reason, the permittee does not comply with or will be unable to comply with any condition or limitation specified in this permit, the permittee shall immediately provide the Department with the following information: A description of and cause of noncompliance; and The period of noncompliance, including dates and times; or, if not corrected, the anticipated time the noncompliance is expected to continue, and steps being taken to reduce, eliminate, and prevent recurrence of the noncompliance. The permittee shall be responsible for any and all damages which may result and may be subject to enforcement action by the Department for penalties or for revocation of this permit. Comments: The facility was in compliance with all of the permit conditions at all times, per Mr. Richard Dillen. With my inspection of the facility’s records and walk through the production area, I can state with reasonable amount of certainty that the facility was in compliance with applicable rules and permit conditions. Common Conditions [Rule 62-296.320(4)(c), F.A.C.] Unless otherwise specified in the permit, the following conditions apply to all emissions units and activities at the facility. Emissions and Controls 2. Circumvention: The permittee shall not circumvent the air pollution control equipment or allow the emission of air pollutants without this equipment operating properly. [Rule 62-210.650, F.A.C.] Comments: The facility does not have pollution control equipment. 6. VOC or OS Emissions: No person shall store, pump, handle, process, load, unload or use in any process or installation, volatile organic compounds (VOC) or organic solvents (OS) without applying known and existing vapor emission control devices or systems deemed necessary and ordered by the Department. [Rule 62-296.320(1), F.A.C.] Comments: In my tour throughout the property, there were no leaks from the stationary tanks, the truck tanks, pipes or drums in the facility. The entire yard was very clean, including the oil filter recycling area. 7. Objectionable Odor Prohibited: No person shall cause, suffer, allow or permit the discharge of air pollutants, which cause or contribute to an objectionable odor. An “objectionable odor” means any odor present in the outdoor atmosphere which by itself or in combination with other odors, is or may be harmful or injurious to human health or welfare, which unreasonably interferes with the comfortable use and enjoyment of life or property, or which creates a nuisance. [Rules 62-296.320(2) and 62-210.200(Definitions), F.A.C.] Comments: An upwind/downwind survey of the facility was conducted. The Air Strippers were not operating at the time and neither were the Oil Heater or the “Oil Cooker”. Mr Dillen stated that business was down significantly to somewhere between 50 to 60 % of one year ago. While walking through the Yard, I detected Mercaptans odor at the level of 2-3 (mild). The wind was blowing out of the North, with flags completely unfurled and straight at a right angle to the pole. The wind speed at ground level was somewhere between 3-5 miles per hour, but at the flag level (about 50 feet from the ground for the 2 flags that I could see) I estimate that the wind was blowing at around 10 – 15 mph due South. On 3/25/10, I called Mrs. Mildred Reese who has complained about odors in the area, which she has attributed to HOWCO. I informed Mrs. Reese that I inspected HOWCO on 3/23/10 and HOWCO was not operating the Air Strippers, the Oil Heater or the Oil Cooker. I also informed her that despite that, on the HOWCO property, I was able to detect Mercaptans which were obviously emanating from the gas relief valves of the People’s Gas Co. that run along 43rd Street and across 8th and 9th Avenues. I pointed out to Mrs. Reese that the Gas Pipeline Relief valves have the purpose of releasing excessive pressure in the Pipeline to avoid ruptures that would potentially present other risks and safety problems. 9. Unconfined Particulate Emissions: No person shall cause, let, permit, suffer or allow the emissions of unconfined particulate matter from any activity, including vehicular movement; transportation of materials; construction, alteration, demolition or wrecking; or industrially related activities such as loading, unloading, storing or handling; without taking reasonable precautions to prevent such emissions. Any permit issued to a facility with emissions of unconfined particulate matter shall specify the reasonable precautions to be taken by that facility to control the emissions of unconfined particulate matter. Reasonable precautions include the following: Paving and maintenance of roads, parking areas and yards. Application of water or chemicals to control emissions from such activities as demolition of buildings, grading roads, construction, and land clearing. Application of asphalt, water, oil, chemicals or other dust suppressants to unpaved roads, yards, open stock piles and similar activities. Removal of particulate matter from roads and other paved areas under the control of the owner or operator of the facility to prevent reentrainment, and from buildings or work areas to prevent particulate from becoming airborne. Landscaping or planting of vegetation. Use of hoods, fans, filters, and similar equipment to contain, capture and/or vent particulate matter. Confining abrasive blasting where possible. Enclosure or covering of conveyor systems. Comments: There were no unconfined particulate or fugitive dust emissions. Administrative Requirements 7 Annual Operating Report: On or before April 1 of each year, the permittee shall submit a completed DEP Form 62-210.900(5), "Annual Operating Report for Air Pollutant Emitting Facility" (AOR) for the preceding calendar year. The report may be submitted electronically in accordance with the instructions received with the AOR package sent by the Department, or a hardcopy may be sent to the Compliance Authority. [Rule 62-210.370(3), F.A.C.] Comments: The annual operating report for calendar year 2099 was submitted on March 23rd, 2010. 8 Operation Permit Renewal Application: A completed application for renewal of the operation permit shall be submitted to the Permitting Authority with a copy to PCDEM (Compliance Authority) no later than 60 days prior to the expiration date of the operation permit. [Rules 62-4.030, 62-4.050, 62-4.070(3), 62-4.090, 62-210.300(2), and 62-210.900, F.A.C.] Comments: The permit expires on 1/31/11. An application is required to be submitted no later than 12/2/10. Mr. Dillen and I read this permit condition together and he stated that he understood the requirement and did not have any questions. A.1. Fugitive VOC/Organic Solvents (OS): The permittee shall not store, pump, handle, process, load, unload, or use in any process or installation, volatile organic compounds (VOC), Hazardous Air Pollutants (HAPs), or organic solvents without applying known and existing vapor emission control devices or systems deemed necessary and ordered by the Department. The following procedures shall be utilized to minimize pollutant emissions: a. maintain tightly fitting cover, lids, etc. on all containers of OS/VOC/HAPs when they are not being handled, tapped, etc.; b. all VOC/HAPs fittings, valve lines, etc. shall be properly maintained; c. all VOC/HAPs spills shall be attended to immediately and the waste properly disposed of, recycled, etc.; d. all solvent from solvent washings (equipment clean-up) shall be directed into containers that prevent evaporation to the atmosphere; and e. prevent excessive air turbulence across exposed VOC/OS. [Rule 62-296.320(1), F.A.C.] Comments: The facility yard was clean. I examined the Tank Farm and the tank containment areas were dry as were the tanks themselves. The tanks and their respective pipelines were whole and I they did not have corrosion, holes or leaks. I did not see any spills or open drums or containers. A.2. Objectionable Odor - The permittee shall not cause, suffer, allow or permit the discharge of air pollutants, which cause or contribute to an objectionable odor. An objectionable odor is any odor present in the outdoor atmosphere which by itself or in combination with other odors, is or may be harmful or injurious to human health or welfare, which unreasonably interferes with the comfortable use and enjoyment of life or property, or which creates a nuisance. [Rules 62-296.320(2) and 62-210.200(181), F.A.C; Pinellas County Code, Section 58-178] Comments: As stated in permit condition No. 7, I detected Mercaptan odors inside and outside of the facility’s property which were emanating from the People’s Gas Company Relief Valves along 43rd Street and 8th and 9th Avenues South. The facility was not operating any equipment at the time of my visit, which Mr. Dillen stated was due to significant diminished business. (in the AC) A.3. Testing Notification: The permittee shall notify the Compliance Authority in writing at least 15 days prior to any required tests. The notification must include the following information: the date, time, and location of each test; the name and telephone number of the facility’s contact person who will be responsible for coordinating the test; and the name, company, and the telephone number of the person conducting the test. {Permitting Note: The notification should also include the relevant emission unit ID No(s)., test method(s) to be used, and pollutants to be tested.} [Rules 62-4.070(3) and 62-297.310(7)(a)9., F.A.C.] Comments: I read the permit condition to Mr. Dillen. A.4. Recordkeeping Retention: All measurements, records, and other data required by this permit shall be documented in a permanent, legible format and retained at the facility for at least 3 years following the date on which such measurements, records, or data are recorded, unless otherwise specified by Department rule. Records shall be made available to the Permitting Authority and Compliance Authority upon request. [Rules 62-4.070(3) and 62-4.160, F.A.C.] Comments: Mr. Dillen provided me with records going back to 2003 which I personally examined. A.5. Recordkeeping Frequency: Daily records shall be completed within 3 business days and monthly records shall be completed by the end of the following month. [Rule 62-4.070(3), F.A.C.] Comments: The daily records were updated on a daily basis. B.3. Air Flow Rates: The minimum airflow for each Air Stripper shall be 1,200 acfm. [Rule 62-4.070(3), F.A.C.] Comments: The airflow rates for Air Strippers 1 & 2 were tested on April 15th, 2009 and yielded 2,197 acfm for Air Stripper No. 1 and 1,280 acfm for Air Stripper No. 2. B.4. Operation Mode: The air strippers are allowed to operate simultaneously. [Rule 62-4.070(3), F.A.C.] Comments: The air strippers were not operating during my visit. B.5. Water Throughput Rate: The water throughput rate to Air Stripper No. 1 and Air Stripper No. 2 shall not exceed 28.0 gpm and 90.0 gpm, respectively. [Rule 62-296.320(1), F.A.C.] Comments: The water throughput was at a high of 77 GPM on January 15th, 2010. The Ir Stripper operated 12 days during the month of January 2010. B.6. Mist Control Mechanism: To ensure that there is no mist carry-over impacting the surrounding area, each air stripper shall have adequately sized de-mister pads in the air stripper tower. [Rule 62-4.070(3), F.A.C.] Comments: The de-mister pads were in place. Mr Dillen stated that there was no mist-carry-over. The Air Strippers were not operating at the time of my visit. B.7. Emission Rates: The air strippers shall not exceed the following: a. The total VOC/OS emissions from Air Stripper No. 1 shall not exceed 1.0 tons per any consecutive 12-month period. b. The total VOC/OS emissions from Air Stripper No. 2 shall not exceed 5.0 tons per any consecutive 12-month period. c. The total VOC/OS emissions from both air strippers combined shall not exceed 6.0 tons per any consecutive 12-month period. {Permitting Note: Organic solvent (OS) emissions are included in the total emission limitations, since the EPA Methods used to analyze the waste water, as required by Specific Condition No. B.8., do not separate volatile organic compounds (VOC) from the organic solvents (OS) that are not considered volatile organic compounds (VOC). [Rule 62-210.200(PTE), F.A.C.] Comments: The 12 month running cumulative total VOC emissions from EU 001 (Stripper No. 1) were 6.5304 lbs at the end of the month of January 2010. The 12 month running cumulative total VOC emissions from EU 002 (Stripper No. 4) were 320.5245 lbs at the end of the month of January 2010. The 12 month running combined cumulative total VOC emissions from EUs 001 (Stripper No. 1) and EU 004 (Stripper No. 2) were 327.0549 lbs at the end of the month of January 2010. The former are all in compliance with permit condition B.7. B.8. VOC/OS Concentration in Wastewater Test Methods: In order to demonstrate compliance with Specific Condition No. B.7., the batch waste water throughput shall be analyzed monthly using the appropriate EPA Method such as 601, 602, 625, etc. (see 40 CFR 136.3, Table 1C) prior to entering each air stripper (influent), and after exiting (treatment) each air stripper (effluent). Note: The results of the effluent analysis for Air Stripper No. 2 cannot be used as the analysis results for the influent to Air Stripper No. 1. [Rule 62-4.070(3), F.A.C.] Comments: The facility testing was in compliance with permit condition No. B.8. B.9. Stripper Air Flow Testing Requirements: Required tests and test reports shall be in accordance with the requirements of Appendix D (Common Testing Requirements) of this permit. The stack airflow of each air stripper shall be tested annually within 60 days prior to or on the date of May 30 in accordance with the test method shown below and the test report shall also include the information required below: Method(s) Description of Method and Comments 1 and 2 Traverse Points and Velocity and Flow Rate The above method(s) are described in Appendix A of 40 CFR 60 and are adopted by reference in Rule 62-204.800, F.A.C. No other method(s) may be used unless prior written approval is received from the Department. The test report for each air stripper shall be submitted to the Compliance Authority and shall include the following: a. The associated pressure drop (delta P in inches of water). b. For Air Stripper No. 1 - A copy of the recorder's circular chart, which measures the wastewater flow rate for each day testing occurs. c. A copy of the monthly records required by Specific Condition No. B.11. for the month the tests were conducted. [Rules 62-4.070(3), 62-297.310(8), 62-204.800 and 62-297.100, F.A.C.; and Appendix A of 40 CFR 60] MONITORING REQUIREMENTS B.10. Water Flow Rate Monitoring: The permittee shall comply with the following: a. The water flow rate in gallons per minute (gpm) to Air Stripper No. 1 shall be continuously monitored and recorded on monitor’s circular chart. The monitor’s recordings shall be obtained from the measurements on the upstream side for Air Stripper No. 1 and the downstream side of the holding tank. b. The water flow rate in gallons per minute (gpm) to Air Stripper No. 2 shall be determined from each batch by manually recording the amount of water in gallons and the total time in minutes of transferring the batch of water. [Rule 62-4.070(3), F.A.C.] Comments: The facility was in compliance with a., b., and c. in B.9 and a. and b. in B.10 above. B.11. Operating and VOC/OS Emission Records: In order to document compliance with the requirements of Specific Condition Nos. B.5., B.7., B.8., and B.10., the permittee shall keep records (Batch VOC/OS Report) which contain the following information: DAILY a. Facility Name, Facility ID No., Emission Unit ID No., Emission Unit Description, and Date (month/day/year). b. The start and end operating times, and total operating hours for each air stripper. c. The gallons/day of water through each air stripper. Gallons/hour of water through Air Stripper No. 1 shall be documented by the circular chart of the continuous monitor's recorder. d. The pressure drop (in inches of H2O) across each of the air strippers. MONTHLY e. Facility Name, Facility ID No., Emission Unit ID No., Emission Unit Description, and Date (month/year) f. A monthly total (hours/month) and a cumulative consecutive 12-month period total (hours/consecutive 12-month period) of air stripper operating hours for each air stripper. g. The concentration levels of each pollutant in the influent and effluent based on laboratory gas chromatograph results. h. The monthly (pounds/month) and consecutive 12-month period total (tons/most recent consecutive 12-month period) of VOC/OS emissions for each air stripper; i. A combined (Air Stripper No. 1 + Air Stripper No. 2) consecutive 12-month total of VOC/OS emissions (tons/most recent consecutive 12-month period). Other supporting documentation, such as quantitative analysis of the contaminated water, and gas chromatograph results (as presented in the laboratory reports) which gives the concentration levels of each pollutant in the influent and effluent, shall also be retained and made available at the facility. [Rule 62-4.070(3), F.A.C.] Comments: The facility was in compliance with the record-keeping requirements above. (see records attached) |
|  |  |  | Valid Permit [Rule 62-210.300] |
|  |  |  | Changes to Facility/emission unit [Rule 62-210.300] Does the emission unit description above match what the facility is operating. Yes No Comments: NA |
| ( | C. Other: |
| Pollution Prevention Activities P2 Handouts Provided: P2 Brochure; P2 Manual; P2 Checklist Have any emissions reductions occurred Yes / No Chemical Substitution; Equipment Changes; Process Changes Chemical/Material Reuse; On-site Recycling; Other: Comments: Emission reductions have resulted from a slow-down in orders. |
| Closing Conference: I informed Mr. Dillen that the facility was in compliance with applicable rules and permit conditions. |
| Inspector(s): Jose Rodriguez, Pinellas County, Air Quality Division |
| Signature(s): Date: | Date: 30 March 2010 |
| ACCESS? |  | EASIIR? |  |

H:\users\wpdocs\airqual\Air_Compliance\AQI\1030153 004 71064.doc