INSPECTION REPORT

AIR POLLUTANT EMISSION SOURCES

| FACILITY Pinellas County Utilities—South Cross Bayou WWTP TITLE V | DISTRICT Southwest | COUNTY Pinellas |
| --- | --- | --- |
| ADDRESS 5900 74th Street North St. Petersburg, FL | CONTACT(S) James R. Rolston, Director of Operations, (727) 582-2300; Owner/Auth Rep Gary Glascock; Plant Manager; (727) 582-7000; Facility Contact |
| AIRS ID# 1030234 | PERMIT # 1030234-001-AC | EXPIRATION DATE 3/30/2006 | ARMS ENTRY DATE April 14, 2005 |
| SOURCE DESCRIPTION EU001: Unregulated fugitive VOC emissions from existing WWTP EU002: Two Dried Sewage Sludge (Pellet) Storage Silos EU003: Truck Loading/Unloading Station | EU004: Dryer/Pelletizer Building EU005: Dewatering Building EU006: Sewage Sludge Dryer |
| INSPECTION DATE April 14, 2005 | AUDIT TYPE INS2 | COMPLIANCE STATUS IN COMPLIANCE |
| INSPECTION FINDINGS |
| FACILITY-WIDE CONDITIONS |
| PARAMETER | ALLOWED VALUE | OBSERVATION |
| 1. Objectionable odor (Specific Condition 3 (SC 3)) | Prohibited | None noted during inspection. |
| 2. General visible emissions/ particulate standard (SC 4&6) | Except as otherwise specified by rule or permit condition, 20% opacity. Must observe reasonable precautions. | In compliance. Most areas are covered by structures or pavement. |
| 3. General VOC/OS rule (SC 5) | Must apply known and existing control devices | In compliance. |
| 4. Record keeping (SC 15) | Must be kept 5 years. Daily records complete within 7 days, monthly by end of following month. | In compliance. |
| EMISSION UNIT 006—SEWAGE SLUDGE DRYER |
| PARAMETER | ALLOWED VALUE | OBSERVATION |
| 1. Capacity (SC A.1) | a. 21 tons/hr of total material input, daily average b. Determine %M, %C, and %R at least once per day. c. Determine daily and hourly input rates. | In compliance. Records are being kept. |
| 2. Fuels allowed (SC A.2&3) | a. Natural gas and/or digester gas for dryer furnace at 16.0 MMBtu/hr. b. Only natural gas for thermal oxidizer at 2.0 MMBtu/hr. | In compliance. |
| 3. Exit temperature (SC A.4) | Air exiting RTO’s combustion chamber 1400°F. | In compliance. |
| 4. VE limit (SC A.6, 13) | 5%, except VE not exceeding 20% allowed for 3 minutes in any hour. Test for at least 60 minutes. | In compliance. No visible emissions during inspection. |
| 5. Record keeping (SC A.20) | a. Daily: Date and emission unit number; total input in tons; total operating hours; daily average input rate; baghouse pressure drop; scrubber liquor flow rate; and pressure drop across scrubber. b. Monthly: Month and EU ID; total natural gas to furnace and RTO in ft3; total digester gas to furnace in ft3; total operating hours; and monthly average heat input rate to furnace and RTO in MMBtu/hr; | Records are being kept as required. |
| EMISSION UNIT 002—TWO DRIED SEWAGE SLUDGE (PELLET) STORAGE SILOS |
| PARAMETER | ALLOWED VALUE | OBSERVATION |
| 1. Capacity (SC B.1&2) | a. Maximum transfer rate to each silo is 1.25 tons/hr b. Total transfer to both silos not to exceed 30 tons/day and 10,950 tons in any consecutive 12 months. | In compliance. |
| 2. Record keeping (SC B.4) | a. Daily: Date and EU ID number; baghouse P; tons of pellets transferred; total hours transferring pellets; and average transfer rate in tons/hr. b. Monthly: Most recent consecutive 12 month total pellets transferred in tons. | Records are being kept as required. |

| EMISSION UNIT 003—TRUCK LOADING/UNLOADING STATION |
| --- |
| PARAMETER | ALLOWED VALUE | OBSERVATION |
| 1. Transfer rate (SC C.1&2) | 50 tons/hr to each truck. Only one truck may be loaded at any one time. | In compliance. |
| 2. Recordkeeping (SC C.3) | Daily: Date and EU ID number; chemical coating name and coating rate in gallons/ton; P across baghouse; and for each truck, tons loaded, elapsed loading time, and loading rate in tons/hr. | Records are being kept as required. |
| EMISSION UNIT 004—DRYER/PELLETIZER BUILDING |
| PARAMETER | ALLOWED VALUE | OBSERVATION |
| 1. Control device (SC D.1) | The odor control scrubber shall be operating when the sewage sludge dryer is in operation and/or wet sludge cake is being transferred to the wet cake storage bin. | In compliance. |
| 2. Recordkeeping (SC D.2) | When scrubber is operating, record daily: Date and EU ID number; name of scrubbing liquids; pH of the scrubbing liquid; liquid flow in gallons/minute; and P across the scrubber. | Records are being kept as required. |
| EMISSION UNIT 005—DEWATERING BUILDING |
| PARAMETER | ALLOWED VALUE | OBSERVATION |
| 1. Control device (SC E.1) | The odor control scrubber shall be operating when transferring dried pellets to silos, loading or unloading trucks, or when any equipment associated with the sewage residual handling equipment is in operation. | In compliance. |
| 2. Recordkeeping (SC E.2) | When scrubber is operating, record daily: Date and EU ID number; name of scrubbing liquids; pH of the scrubbing liquid; liquid flow in gallons/minute; and P across the scrubber. | Records are being kept as required. |
| COMMENTS Walked through facility and discussed permit with Mr. Glascock, Mr. Clyde Harris (Plant Manager for the company which operates the pelletizing operation), and Mr. Michael Engelmann (Sr. Engineer for Pinellas County Utilities, who is working to get the operating permit; he also fills out the Annual Operating Report for this facility). Discussed the ongoing effort to complete and issue a Title V operating permit, including the O&M Plan submittal. The discussion revealed that the submittal is actually only a small portion of the total O&M Plan for this facility (the entire plan fills several binders, so they just sent enough to fulfill what they saw as the minimum to satisfy the requirement. Mr. Engelmann will send me two CDs containing the complete plan. |
| INSPECTOR(S) NAME(S) Joseph H. Cox, Jr. |
| SIGNATURE(S) | DATE April 14, 2005 |