INSPECTION REPORT

AIR POLLUTANT EMISSION SOURCES

| FACILITY Polk County North Central Landfill TITLE V FACILITY | DISTRICT Southwest | COUNTY Polk |
| --- | --- | --- |
| ADDRESS 7425 Highway 540 Winter Haven, FL 33880 | CONTACT(S) Allan Choate, P.E., Environmental Engineer, 863-284-4319, extension 214. Brooks Stayer, Landill Operations Manager, 863-284-4319. |
| AIRS ID# 1050298 | PERMIT # 1050298-001-AV | EXPIRATION DATE 9/28/2005 | ARMS ENTRY DATE March 30, 2005 |
| SOURCE DESCRIPTION EU001: Municipal Solid Waste Landfill with an open flare EU002: Stationary Diesel Engines EU003: Roads and Earthmoving Operations Note: EUs 002 and 003 are unregulated emission units |
| INSPECTION DATE March 30, 2005 | AUDIT TYPE INS2 | COMPLIANCE STATUS IN COMPLIANCE |
| INSPECTION FINDINGS |
| PARAMETER | ALLOWED VALUE | OBSERVATION |
| 1. Objectionable odor Specific Condition II-2 (SCII-2) | None allowed | None noted. |
| 2. General visible emissions (SCII-3) | <20% opacity (applies to emission units not subject to a specific PM or opacity limit by rule) | No visible emissions during inspection. |
| 3. General VOC/OS limitation (SCII-4) | Must maintain all valves, pipes, fittings, etc. in good operating condition and immediately confine and clean up spills and ensure wastes are in closed containers. | In compliance |
| 4. Unconfined PM emissions (SCII-6) | Must take reasonable precautions to prevent, IAW 62-296.320. Permit requires watering of roads as needed and states that other controls (e.g., paving/maintenance of roads, planting of vegetation, and posting speed limits for vehicles) may be required. | In compliance. Water truck was working unpaved areas and sweeper was working paved roads. |
| 5. Standards for air emissions from municipal solid waste landfills (SCA.2; §60.752) Note: The reference to §60.752 indicates 40 CFR 60.752. | a. Recalculate the NMOC emission rate annually until it is 50 Mg/yr or until landfill is closed. b. Submit design plan within 1 year of reaching the 50 Mg/yr limit. c. Install collection and control system within 30 months after first annual report over the limit. | In compliance. Projected date for reaching 50 Mg/yr is late 2006. |
| 6. Operational standards (SCA.2; §60.753) | a. Collect gas from all cells active 5 years or more. b. Maintain negative pressure at each wellhead. c. Maintain gas temperature <55 °C and either a nitrogen level <20% or an oxygen level <5%. d. Monitor surface methane concentration at 30-meter intervals and maintain at <500 ppm. e. If collection or control system fails, shut down gas mover system and shut all valves within 1 hour. f. Operate control system at all times when gas is routed to the system. | Gas is already being collected and used by Ridge Generating Station; but this landfill does not yet come under many of the rules because it has not yet reached 50 Mg/yr gas production. |

| PARAMETER | ALLOWED VALUE | OBSERVATION |
| --- | --- | --- |
| 7. Compliance provisions (SCA.2; §60.755) | a. Measure gas pressure at each well monthly and respond appropriately to any positive pressures. b. Monitor surface concentrations of methane at 30 meter intervals on a quarterly basis and take specified steps in response to any 500 ppm. Calibrate immediately before each survey. c. Monitor cover integrity monthly and implement repairs as necessary. d. Duration of start-up, shutdown, or malfunction shall not exceed 5 days for collection system and shall not exceed 1 hour for the flare. | N/A. Production is still below 50 Mg/yr. |
| 8. Monitoring of operations (SCA.2; §60.756) | a. Install a sampling port and means to measure temperature at each wellhead. b. Measure gauge pressure, temperature, and either nitrogen or oxygen concentration monthly. c. Install, calibrate, maintain, and operate a flame monitor at the flare. d. Record flow or secure bypass valve in closed position. | N/A. Production is still below 50 Mg/yr. |
| 9. Reporting requirements (SCA.2; §60.757) | a. Submit annual reports of the following: 1. Flare operation and exceedances of pressure, N or O concentration. 2. Length of time for each instance when the flare was not operating for more than 1 hour. 3. Any period of gas collection system not operating for more than 5 days. 4. Location of each exceedance of the 500 ppm methane concentration and the concentration at each location for which there was an exceedance in the previous month. 5. Date of installation and location for each expansion of the collection system. | N/A. Production is still below 50 Mg/yr. |
| 10. Recordkeeping requirements (SCA.2; §60.758) | Recordkeeping is required for the following (see the permit for details): a. Design capacity of the landfill b. Initial performance test or compliance determination c. Equipment operating parameters d. Plot map of collectors e. Collection and control system exceedances of operational standards f. Design capacity recalculations | In compliance. |
| COMMENTS |
| INSPECTOR(S) NAME(S) Joseph H. Cox, Jr. |
| SIGNATURE(S) | DATE March 30, 2005 |