## Dec 2012
SOUTH DISTRICT WASTEWATER TREATMENT PLANT
STAND BY GENERATORS
MONTHLY ELAPSED TIME , KILOWATT- HOUR READINGS & E.M.D. FUEL USED | [23 empty] | JANUARY 2013
| E.T. HOURS | [19 empty] | TONS NOX | KWH | KWH | TOTAL KWH | E.M.D.
| E.M.D'.s | [15 empty] | GAS |  |  |  | EMITTED | FOR | FOR | GAS | TOTAL
DATE | SWITCHGEAR BUILDING # 1 | [6 empty] | SWITCHGEAR BUILDING # 2 | [7 empty] | TOTAL | GENERATOR |  |  | TOTAL | FOR | DIESEL | GAS | & | DIESEL
| # 1 | # 2 | # 3 | # 4 | # 5 | # 6 | TOTAL | # 1 | # 2 | # 3 | # 4 | # 5 | # 6 | # 7 | TOTAL | 1 & 2 | # 1 | # 2 | # 3 |  | GAS * |  |  | DIESEL | USED
Jan 2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 552 | 724 | 1276 | 6.1886 | 0 | 1066800 | 1066800 | 82
Feb 2012 | 7 | 8 | 8 | 8 | 6 | 2 | 39 | [8 empty] | 39 | 0 | 505 | 592 | 1097 | 5.3205 | 1200 | 928200 | 929400 | 3361
Mar 2012 | 13 | 13 | 7 | 0 | 13 | 12 | 58 | [8 empty] | 58 | 0 | 93 | 717 | 810 | 3.9285 | 2400 | 659400 | 661800 | 5585
April 2012 | 4 | 5 | 5 | 4 | 7 | 4 | 29 | [8 empty] | 29 | 0 | 585 | 138 | 723 | 3.5065 | 0 | 604800 | 604800 | 2266
May 2012 | 1 | 1 | 1 | 1 | 1 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 632 | 496 | 1128 | 5.4708 | 0 | 936600 | 936600 | 235
June 2012 | 2 | 0 | 1 | 2 | 1 | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 656 | 676 | 1332 | 6.4602 | 0 | 1041600 | 1041600 | 611
July 2012 | 2 | 5 | 4 | 3 | 4 | 1 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 507 | 691 | 1198 | 5.8103 | 1200 | 966000 | 967200 | 1735
Aug 2012 | 61 | 87 | 66 | 66 | 98 | 94 | 472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 472 | 0 | 483 | 610 | 1093 | 5.301 | 141600 | 890400 | 1032000 | 54029
Sep 2012 | 3 | 5 | 4 | 5 | 7 | 4 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 551 | 588 | 1139 | 5.5241 | 1200 | 907200 | 908400 | 1580
Oct 2012 | 2 | 1 | 1 | 1 | 1 | 33 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 547 | 599 | 1146 | 5.5581 | 120000 | 936600 | 1056600 | 579
Nov 2012 | 6 | 10 | 10 | 10 | 3 | 4 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 559 | 668 | 1227 | 5.9509 | 1200 | 1012200 | 1013400 | 3985
Dec 2012 | 3 | 4 | 3 | 4 | 3 | 4 | 21 | 5 | 8.3 | 8.2 | 3.3 | 12.8 | 12.2 | 12.3 | 62.1 | 83.1 | 0 | 241 | 628 | 869 | 4.2146 | 0 | 726600 | 726600 | 8866.5
TOTAL | 104 | 139 | 110 | 104 | 144 | 161 | 762 | 5 | 8.3 | 8.2 | 3.3 | 12.8 | 12.2 | 12.3 | 62.1 |  | 0 | 5911 | 7127 |  |  | 268800 | 10676400 | 10945200
TOTALS | [15 empty] | 824.1 |  |  |  | 13038 | 63.2343 |  |  | 10945200 | 82914.5
|  |  | PERMIT MAXIMUM |  |  |  | N/A | [9 empty] | 12 Consecutive months |  |  | 19000 | 92.15 |  | 365 day rolling total |  | 425000
* NOX CALCULATION BASED ON PERMIT LIMITATION OF 9.7 lbs/hrs