| FACILITY INFORMATION |
| --- |
| Facility Name: Bethesda Memorial Hospital |
| ARMS ID No.: 099-0095 | Air Permit No.: 0990095-005-AV | Expires: 1/1/2012 |  |
| Facility Contact: Bruce Mandigo Phone: 561-737-7733 | Title: Director of Facility – Mgmt. |
| Inspection Summary |
| Inspection Date: 3/16/2010 | Inspector: Paul Kalamaras/Laxmana Tallam |
| Report Date: | Signature: |
| Inspection Type: INSP3 – Witness Stack Test | Inspection Subtype: Medical Waste Incinerator |
| Compliance Status; IN | ARMS Updated: | Approval/Date: |
| Facility: Arrived at 10:45 Departed at 12:15 |

| Emission Unit Inspection Details |
| --- |
| EU No. | Compliance IN MNC SNC | Inspection Observations and Comments |
| EU 4 | IN | Readings taken at 10:50 during Second Stack Test Run Maximum Charge Rate Allowed (lbs/hr) Bethesda Hospital 1000 lb/hr limit Readings taken (1hr) 10:50 11:30 Limits Charge Rate: 966 874 1000 lb/hr Secondary Temperature 1983 2005 1800F min. Scrubber Amps: 57.3 57.1 56 amps min. Scrubber Flow: 271 271 230 GPM min. Scrubber PH: 7.2 7.2 Min 6.7 CO: 1 0 100 ppm max. Shall not exceed 5% of the total annual allowable hours of oper. (4416) Hours of Operation, Qtr: N/A 4,416 hrs. max/yr Bypass Downtime, Qtr: N/A 20 hrs. max/yr |
| EU04 | IN | The first stack test run was from 8:49 to 9:52, The filter box temp was 249 deg F. Leak check passed and witnessed test while asking questions to the tester on how the parameters were read from the testing equipment as well as temperature of gas plume and stack temperature. The tester was knowledgeable in conducting the stack test. Filter was examined after 1st run and appeared clear. Very little PM residue on filter. Conducted VE test mostly during the second test run for ~25 mins. VE showed 0% values with a few 5% readings occurring roughly every 5 minutes or so. Second Test run was conducted 10:05 to 11:08. Test was going well within normal parameter values. |