| 1030011 006 62587 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| FACILITY: Progress Energy Florida, Inc. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PERMIT ID: 73 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Florida Power, Bartow Plant |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DISTRICT: Southwest |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ADDRESS: 1601 Weedon Island Drive |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CONTACT PHONE: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| St. Petersburg, FL |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 727-826-4130 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ARMS NO: 1030011 006 |  |  |  |  |  |  |  | PERMIT NO: |  |  |  |  |  |  |  |  |  |  |  | Expiration Date: 12/31/09 Renewal Date: 5/20/09 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | 1030011-009-AV |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Test Due Date: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| EMISSION UNIT DESCRIPTION : Peaking Unit No. 2: General Electric Company, Model MS 7000, Serial No. 217711 Gas Turbine |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| INSPECTION DATE: |  |  |  |  |  |  | ARMS INSPECTION TYPE: |  |  |  |  |  |  |  |  |  |  |  |  |  |  | COMPLIANCE STATUS: |  |  |  |  |  |  |  |  |  |  |  |  |
|  | June 17, 2008 |  |  |  |  |  |  |  |  | INS1 |  |  | INS2 |  |  | INS3 |  |  | FUI |  |  |  |  |  | IN |  |  | MNC |  |  |  |  | SNC |  |
| INSPECTION TYPE: |  |  |  |  | Initial |  |  |  |  |  | Re-inspection |  |  |  |  |  | Complaint |  |  |  |  |  |  | Drive-by |  |  |  |  |  | Quarterly |  |  |  |  |
|  |  |  | A. General Review: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1. |  | Permit File Review |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  |  |  | No |
|  |  | Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2. |  | Introduction and Entry |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  |  |  | No |
|  |  | Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3. |  | Is the Responsible Official/Authorized Representative still: Tom Lawery? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  |  |  | No |
|  |  | Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4. |  | Is the facility contact still: Scott Stenger, Steve Ryan, Dave Meyer? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  |  |  | No |
|  |  | Comments: The facility contacts are Terese Sanchez and Charles Dufeny. The person in charge of the Peakers and the contact of the Peakers is Gus Schaefer. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| IN | MNC | SNC | B. Specific Conditions: |
| --- | --- | --- | --- |
|  |  |  | Section II. Facility-wide Conditions. This permit or a copy thereof shall be kept at the work site of the permitted activity. [APPENDIX TV-4, TITLE V CONDITION 12(12)] Comments: The facility had copy of the permit at the work-site. Renewals. Prior to one hundred eighty (180) days before the expiration of a permit issued pursuant to Chapter 62-213, F.A.C., the permittee shall apply for a renewal of a permit using forms incorporated by reference in the specific rule chapter for that kind of permit. [APPENDIX TV-4, TITLE V CONDITION 5] Comments: The permit application is due to be submitted on, or before 7/5/09. I read the permit condition to Mr. Gus Schaefer. 2. General Pollutant Emission Limiting Standards. Objectionable Odor Prohibited. The permittee shall not cause, suffer, allow, or permit the discharge of air pollutants which cause or contribute to an objectionable odor. [Rule 62-296.320(2), F.A.C] Comments: An upwind/downwind survey of the facility was conducted. The observed parameters were: Downwind odor detected- none; Wind direction - South Upwind odor detected-none. 3. General Particulate Emission Limiting Standards. General Visible Emissions Standard - Except for emissions units that are subject to a particulate matter or opacity limit set forth or established by rule and reflected by conditions in this permit, no person shall cause, let, permit, suffer or allow to be discharged into the atmosphere the emissions of air pollutants from any activity, the density of which is equal to or greater than that designated as Number 1 on the Ringelmann Chart (20 percent opacity). EPA Method 9 is the method of compliance pursuant to Chapter 62-297, F.A.C. [Rules 62-296.320(4)(b)1. & 4., F.A.C.] Comments: The Peakers were not in operation at the time of my inspection. I did not perform a VE Test. 4. Prevention of Accidental Releases (Section 112(r) of CAA). If required by 40 CFR 68, the permittee shall submit to the implementing agency: A. A risk management plan (RMP) when, and if, such requirement becomes applicable; and B. Certification forms and/or RMPs according to the promulgated rule schedule. [40 CFR 68] Comments: A Risk Management Plan (RMP) was submitted with the original Title V application and is on file. 7. General Pollutant Emission Limiting Standards. Volatile Organic Compounds (VOC) Emissions or Organic Solvents (OS) Emissions. The permittee shall allow no person to store, pump, handle, process, load, unload or use in any process or installation, volatile organic compounds (VOC) or organic solvents (OS) without applying known and existing vapor emission control devices or systems deemed necessary and ordered by the Department. “Nothing was deemed necessary and ordered at this time.” [Rule 62-296.320(1)(a), F.A.C.] Comments: The Peakers operate on Natural Gas. There are no controls. No other VOC are handled at this facility as part of the process. 8. Emissions of Unconfined Particulate Matter. Pursuant to Rules 62-296.320(4)(c)1., 3. & 4., F.A.C., reasonable precautions to prevent emissions of unconfined particulate matter at this facility include the following requirements (see Condition 57. of APPENDIX TV-4, TITLE V CONDITIONS): The following requirements are “not federally enforceable”: a. Maintenance of paved areas as needed; b. Regular mowing of grass and care of vegetation; and, c. Limiting access to plant property by unnecessary vehicles. [Rule 62-296.320(4)(c)2., F.A.C.; and, proposed by the applicant in the initial Title V permit application received June 14, 1996] Comments: The paved areas were being maintained. There were no fugitive dust plumes and the vegetation and grassy areas appeared to be maintained, as well. 10. Statement of Compliance. The annual statement of compliance pursuant to Rule 62-213.440(3)(a)2., F.A.C., shall be submitted to the Department and EPA within 60 (sixty) days after the end of the calendar year using DEP Form No. 62-213.900(7), F.A.C. [Rules 62-213.440(3) and 62-213.900, F.A.C.] {Permitting Note: This condition implements the requirements of Rules 62-213.440(3)(a)2. & 3., F.A.C. (see Condition 51. of APPENDIX TV-4, TITLE V CONDITIONS)} Comments: The Statement of Compliance of calendar year 2007 was submitted on February 12th, 2008. ###### Essential Potential to Emit (PTE) Parameters C.1. Permitted Capacity. The maximum operation heat input rates are as follows: Unit No.; MMBtu/hr Heat Input; Fuel Type. P-2; 714; Natural Gas. [Rules 62-4.160(2) and 62-210.200(PTE), F.A.C.] Comments: Regular record keeping is not required for heat input. Instead the owner or operator is expected to determine heat input whenever emission testing is required, to demonstrate at what percentage of the rated capacity the unit was tested. C.3. Methods of Operation - Fuels. Only natural gas and/or new No. 2 fuel oil shall be fired in the combustion turbines. New No. 2 fuel oil is defined as fuel oil that has been refined from crude oil and has not been used and which may or may not contain additives. [Rule 62-213.410(1), F.A.C.; and, AO 52-253215A, AO 52-253216A, AO 52-253217A, and AO 52-253218A] Comments: EU 006 operated for 852 hours on NG and 44 on No2 Fuel Oil for the last 12 months from 6/25/07-6/24/08. ###### Emission Limitations and Standards C.5. Visible Emissions. Visible emissions from each turbine shall not be equal to or greater than 20 percent opacity. [Rule 62-296.320(4)(b)1., F.A.C.; and, AO 52-253215A, AO 52-253216A, AO 52-253217A, and AO 52-253218A] Comments: The Peakers were not operating at the time of my visit. I did not perform a Method 9 VE. C.6. Not federally enforceable. Sulfur Dioxide - Sulfur Content. The sulfur content of the No. 2 fuel oil shall not exceed 0.5 percent, by weight. [AO 52-253215A, AO 52-253216A, AO 52-253217A, and AO 52-253218A] ###### C.9. Not federally enforceable. The permittee shall demonstrate compliance with the liquid fuel sulfur limit by means of a fuel analysis provided by the vendor upon each fuel delivery. See specific condition Monitoring of Operations C.9. Not federally enforceable. The permittee shall demonstrate compliance with the liquid fuel sulfur limit by means of a fuel analysis provided by the vendor upon each fuel delivery. C.12. The fuel sulfur content, percent by weight, for liquid fuels shall be evaluated using either ASTM D2622-92, ASTM D4294-90, both ASTM D4057-88 and ASTM D129-91, or latest edition, or ASTM D1552-95 or an equivalent method after Department approval. [Rules 62-213.440 and 62-297.440, F.A.C.] Comments: The % Sulfur content of the No. 2 Fuel Oil used for the first 5 months of 2008 was 0.34 %. The fuel sulfur content, percent by weight was determined using ASTM D1552-95. (see COA attached) ###### Excess Emissions {Permitting note: The Excess Emissions Rule at Rule 62-210.700, F.A.C., cannot vary any requirement of a NSPS or NESHAP provision.} C.7. Excess emissions from these emissions units resulting from startup, shutdown or malfunction shall be permitted provided that best operational practices to minimize emissions are adhered to and the duration of excess emissions shall be minimized but in no case exceed two hours in any 24 hour period unless specifically authorized by PCDEM for longer duration. [Rule 62-210.700(1), F.A.C.] C.8. Excess emissions which are caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure which may reasonably be prevented during startup, shutdown or malfunction shall be prohibited. [Rule 62-210.700(4), F.A.C.] Comments: There were no periods of excess emissions, per Mr. Gus Schaefer, in the last 12 months. C.2. Emissions Unit Operating Rate Limitation After Testing. See specific condition C.13. [Rule 62-297.310(2), F.A.C.] AND C.13. Operating Rate During Testing. Testing of emissions shall be conducted with the emissions unit operating at permitted capacity. Permitted capacity is defined as 90 to 100 percent of the peak heat input rate based on the average turbine inlet temperature during the test. The peak heat input rate is defined by a graph of Fuel Heat Input verses Ambient Temperature for each gas turbine. If it is impracticable to test at permitted capacity, an emissions unit may be tested at less than the minimum permitted capacity (i.e., at less than 90 percent of the maximum operation rate allowed by the permit); in this case, subsequent emissions unit operation is limited to 110 percent of the test load until a new test is conducted, provided however, operations do not exceed 100 percent of the maximum operation rate allowed by the permit. Once the emissions unit is so limited, operation at higher capacities is allowed for no more than 15 consecutive days for the purpose of additional compliance testing to regain the authority to operate at the permitted capacity. [Rules 62-297.310(2), F.A.C.; and, AO 52-253215A, AO 52-253216A, AO 52-253217A, and AO 52-253218A] Comments: This EU operated 852 hours on NG and 44 on No2 Fuel Oil for the last 12 months from 6/25/07-6/24/08. C.15. Frequency of Compliance Tests. The following provisions apply only to those emissions units that are subject to an emissions limiting standard for which compliance testing is required. (a) General Compliance Testing. 3. The owner or operator of an emissions unit that is subject to any emission limiting standard shall conduct a compliance test that demonstrates compliance with the applicable emission limiting standard prior to obtaining a renewed operation permit. Emissions units that are required to conduct an annual compliance test may submit the most recent annual compliance test to satisfy the requirements of this provision. In renewing an air operation permit pursuant to Rule 62-210.300(2)(a)3.b., c., or d., F.A.C., the Department shall not require submission of emission compliance test results for any emissions unit that, during the year prior to renewal: a. Did not operate; or b. In the case of a fuel burning emissions unit, burned liquid fuel for a total of no more than 400 hours. 4. During each federal fiscal year (October 1 - September 30), unless otherwise specified by rule, order, or permit, the owner or operator of each emissions unit shall have a formal compliance test conducted for: a. Visible emissions, if there is an applicable standard; b. Each of the following pollutants, if there is an applicable standard, and if the emissions unit emits or has the potential to emit: 5 tons per year or more of lead or lead compounds measured as elemental lead; 30 tons per year or more of acrylonitrile; or 100 tons per year or more of any other regulated air pollutant; and c. Each NESHAP pollutant, if there is an applicable emission standard. 9. The owner or operator shall notify the PCDEM, at least 15 days prior to the date on which each formal compliance test is to begin, of the date, time, and place of each such test, and the test contact person who will be responsible for coordinating and having such test conducted for the owner or operator. (b) Special Compliance Tests. When the PCDEM, after investigation, has good reason (such as complaints, increased visible emissions or questionable maintenance of control equipment) to believe that any applicable emission standard contained in a Department rule or in a permit issued pursuant to those rules is being violated, it may require the owner or operator of the emissions unit to conduct compliance tests which identify the nature and quantity of pollutant emissions from the emissions unit and to provide a report on the results of said tests to the PCDEM. (c) Waiver of Compliance Test Requirements. If the owner or operator of an emissions unit that is subject to a compliance test requirement demonstrates to the Department, pursuant to the procedure established in Rule 62-297.620, F.A.C., that the compliance of the emissions unit with an applicable weight emission limiting standard can be adequately determined by means other than the designated test procedure, such as specifying a surrogate standard of no visible emissions for particulate matter sources equipped with a bag house or specifying a fuel analysis for sulfur dioxide emissions, the Department shall waive the compliance test requirements for such emissions units and order that the alternate means of determining compliance be used, provided, however, the provisions of Rule 62-297.310(7)(b), F.A.C., shall apply. [Rule 62-297.310(7), F.A.C.; and, SIP approved] C.16. Visible Emissions Testing - Annual. By this permit, annual emissions compliance testing for visible emissions is not required for these emissions units while burning: a. only gaseous fuels; or b. gaseous fuels in combination with any amount of liquid fuels for less than 400 hours per year; or c. only liquid fuels for less than 400 hours per year. [Rules 62-297.310(7)(a)4. & 8., F.A.C.] Comments: This EU operated 852 hours on NG and 44 on No2 Fuel Oil for the last 12 months from 6/25/07-6/24/08. According to the interpretation given by the FDEP and AQD Management the facility is only required to test if use of oil is over 400 hours. (see “b.” above). ###### Recordkeeping and Reporting Requirements C.17. Malfunction Reporting. In the case of excess emissions resulting from malfunctions, each owner or operator shall notify the PCDEM in accordance with Rule 62-4.130, F.A.C. A full written report on the malfunctions shall be submitted in a quarterly report, if requested by the Department. [Rule 62-210.700(6), F.A.C.] Comments: There were no malfunctions of the Peakers, per Mr. Gus Schaefer. C.18. Test Reports. (a) The owner or operator of an emissions unit for which a compliance test is required shall file a report with PCDEM on the results of each such test. (b) The required test report shall be filed with PCDEM as soon as practical but no later than 45 days after the last sampling run of each test is completed. [Rule 62-297.310(8), F.A.C.] Comments: There were no tests required at this time. C.19. Not Federally Enforceable. Operating Reports. The annual operating report shall be based on the following: (a) The Btu heating value, sulfur content (percent by weight), API gravity and density of the fuel being fired in the peaking units, shall be based on a weighted 12-month average (calendar year) and be calculated from the fuel delivery receipts and the vendors fuel oil analysis. (b) Until further notice by the PCDEM, Progress Energy Florida shall calculate annual emissions (pounds per hour and tons per year), for the Annual Operating Report, by multiplying the total million Btu from fuel usage by the following emissions factors: Emissions Factors for No. 2 Fuel Oil Pound per MMBtu. Particulate Matter (PM); 0.061 (Total). PM10; 0.48 PM. Carbon Monoxide; 0.048. Sulfur Dioxide; 1.01(S). Nitrogen Oxides; 0.698. Hydrocarbons (TOC); 0.017. “S” denotes sulfur content, percent by weight. The sulfur dioxide emissions shall be based on a weighted 12-month average “S” value. [AO 52-253215A, AO 52-253216A, AO 52-253217A, and AO 52-253218A] Comments: The AOR for 2007 was submitted and the emission factors above were used to calculate emissions. |
|  |  |  | #### Valid Permit [Rule 62-210.300] |
|  |  |  | #### Changes to Facility/emission unit [Rule 62-210.300] Does the emission unit description above match what the facility is operating  Yes No Comments: NA |

|  |  | C. Other: |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Pollution Prevention Activities - P2 Handouts Provided:  P2 Brochure; P2 Manual; P2 Checklist - Have any emissions reductions occurred Yes /  No Chemical Substitution; Equipment Changes; Process Changes Chemical/Material Reuse; On-site Recycling; Other: Comments: There were no changes in chemicals used, processes, equipment or on-site re-cycling. |  |  |  |  |  |  |  |
| Closing Conference: I informed Mr. Schaefer that the EU was in compliance with permit conditions and applicable rules. |  |  |  |  |  |  |  |
| Inspector(s): Jose Rodriguez, Pinellas County, Air Quality Division |  |  |  |  |  |  |  |
| Signature(s): Date: |  |  |  |  |  |  | Date: June 24, 2008 |
|  | # ACCESS? |  |  | # EASIIR? |  |  |  |

/tmp/in/input.doc