| 1030011 003 57517 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| FACILITY: Progress Energy Florida, Inc. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PERMIT ID: 70 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Florida Power, Bartow Plant |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DISTRICT: Southwest |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ADDRESS: 1601 Weedon Island Drive |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CONTACT PHONE: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| St. Petersburg, FL |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 727-826-4130 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ARMS NO: 1030011 003 |  |  |  |  |  |  |  | PERMIT NO: |  |  |  |  |  |  |  |  |  |  |  |  | EXPIRATION DATE: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | 1030011-009-AV |  |  |  |  |  |  |  |  |  |  |  |  | 12/31/09 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| EMISSION UNIT DESCRIPTION : Electric Utility Steam Generator, Unit No. 3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| INSPECTION DATE: |  |  |  |  |  |  | ARMS INSPECTION TYPE: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | COMPLIANCE STATUS: |  |  |  |  |  |  |  |  |  |  |  |  |
|  | May 16, 2007 |  |  |  |  |  |  |  |  |  | INS1 |  |  | INS2 |  |  | INS3 |  |  | FUI |  |  |  |  |  | IN |  |  | MNC |  |  |  |  | SNC |  |
| INSPECTION TYPE: |  |  |  |  | Initial |  |  |  |  |  |  | Re-inspection |  |  |  |  |  | Complaint |  |  |  |  |  |  | Drive-by |  |  |  |  |  | Quarterly |  |  |  |  |
|  |  |  | A. General Review: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1. |  | Permit File Review |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  |  |  | No |
|  |  | Comments: Comments: On May 9th, 2007 the AQD e -mailed Progress Energy details of information that would be required for the inspections during stack testing of Emission Units 001, 002, and 003. Some of the information would be generated during the testing and some of it would have to wait until then. However, other information, such as certificates of analysis and EU # 001 ESP parameters, could be obtained prior to the arrival of AQD personnel. The testing was performed by CEM Solutions, headed by Jeremy Johnson. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2. |  | Introduction and Entry |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  |  |  | No |
|  |  | Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3. |  | Is the Responsible Official/Authorized Representative still: Rufus Jackson? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  |  |  | No |
|  |  | Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4. |  | Is the facility contact still: Scott Stenger, Steve Ryan, Dave Meyer? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  |  |  | No |
|  |  | Comments: The new contacts are Therese Sanchez and Erika Tuchbaum. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| IN | MNC | SNC | B. Specific Conditions: |
| --- | --- | --- | --- |
|  |  |  | Section II. Facility-wide Conditions. This permit or a copy thereof shall be kept at the work site of the permitted activity. [APPENDIX TV-4, TITLE V CONDITION 12(12)] Comments: The facility contact showed me a copy of the permit. Renewals. Prior to one hundred eighty (180) days before the expiration of a permit issued pursuant to Chapter 62-213, F.A.C., the permittee shall apply for a renewal of a permit using forms incorporated by reference in the specific rule chapter for that kind of permit. [APPENDIX TV-4, TITLE V CONDITION 5] Comments: The permit application is due to be submitted on, or before 7/5/09. I read the permit conditions lot the facility contact. -2. General Pollutant Emission Limiting Standards. Objectionable Odor Prohibited. The permittee shall not cause, suffer, allow, or permit the discharge of air pollutants which cause or contribute to an objectionable odor. [Rule 62-296.320(2), F.A.C] Comments: An upwind/downwind survey of the facility was conducted. The observed parameters were: Downwind odor detected- none; Wind direction – East Upwind odor detected-none. 3. General Particulate Emission Limiting Standards. General Visible Emissions Standard - Except for emissions units that are subject to a particulate matter or opacity limit set forth or established by rule and reflected by conditions in this permit, no person shall cause, let, permit, suffer or allow to be discharged into the atmosphere the emissions of air pollutants from any activity, the density of which is equal to or greater than that designated as Number 1 on the Ringelmann Chart (20 percent opacity). EPA Method 9 is the method of compliance pursuant to Chapter 62-297, F.A.C. [Rules 62-296.320(4)(b)1. & 4., F.A.C.] Comments: Visible Emissions will be measured using E PA Method 9. Each Emissions Unit is allowed 40% opacity during steady state operation and 60% opacity during soot blowing. 4. Prevention of Accidental Releases (Section 112(r) of CAA). If required by 40 CFR 68, the permittee shall submit to the implementing agency: A. A risk management plan (RMP) when, and if, such requirement becomes applicable; and B. Certification forms and/or RMPs according to the promulgated rule schedule. [40 CFR 68] Comments: The facility has an R MP plan that was submitted with its permit application. 7. General Pollutant Emission Limiting Standards. Volatile Organic Compounds (VOC) Emissions or Organic Solvents (OS) Emissions. The permittee shall allow no person to store, pump, handle, process, load, unload or use in any process or installation, volatile organic compounds (VOC) or organic solvents (OS) without applying known and existing vapor emission control devices or systems deemed necessary and ordered by the Department. “Nothing was deemed necessary and ordered at this time.” [Rule 62-296.320(1)(a), F.A.C.] Comments: All solvents were kept in containers with tightly fitting lids. 8. Emissions of Unconfined Particulate Matter. Pursuant to Rules 62-296.320(4)(c)1., 3. & 4., F.A.C., reasonable precautions to prevent emissions of unconfined particulate matter at this facility include the following requirements (see Condition 57. of APPENDIX TV-4, TITLE V CONDITIONS): The following requirements are “not federally enforceable”: a. Maintenance of paved areas as needed; b. Regular mowing of grass and care of vegetation; and, c. Limiting access to plant property by unnecessary vehicles. [Rule 62-296.320(4)(c)2., F.A.C.; and, proposed by the applicant in the initial Title V permit application received June 14, 1996] Comments: There is a lot of on-going construction activity at Progress Energy. To keep fugitive dust emissions to a minimum, Progress Energy has a water truck with which the roads on the premises were being watered continuously. 10. Statement of Compliance. The annual statement of compliance pursuant to Rule 62-213.440(3)(a)2., F.A.C., shall be submitted to the Department and EPA within 60 (sixty) days after the end of the calendar year using DEP Form No. 62-213.900(7), F.A.C. [Rules 62-213.440(3) and 62-213.900, F.A.C.] {Permitting Note: This condition implements the requirements of Rules 62-213.440(3)(a)2. & 3., F.A.C. (see Condition 51. of APPENDIX TV-4, TITLE V CONDITIONS)} Comments: The Statement of compliance of calendar year 2006 was submitted on Feb 8th, 2007 Essential Potential to Emit (PTE) Parameters A.1. Permitted Capacity. The maximum operation heat input rates are as follows: E.U. ID No.; MMBTUs/hr Heat Input; Fuel. -003; 2,211; new No. 2 through 6 fuel oil. 2,266; Natural gas. 2,211; On-specification used oil. 2,266; Natural gas and new No. 6 fuel oil and/or on-specification used oil with a maximum of 2,211 MMBTUs/hr from the new No. 6 fuel oil and/or on-specification used oil. [Rules 62-4.160(2), 62-210.200(PTE), 62-296.405 and 62-296.702, F.A.C.] Comments: This EU began operations at 1986.8 MM BTU/hour and ended the run at 1,991.4 MMBTUs / hour. A.3. Methods of Operation. Fuels. The only fuels allowed to be burned are: E.U. ID No.; Fuel. -003; new No. 2 through 6 fuel oil. Natural gas. On-specification used oil. Propane. Each emissions unit may burn the allowed fuels either alone or in any combination. On-Specification used oil containing any quantifiable levels of PCBs can only be fired when the emissions unit is at normal operating temperatures. [Rule 62-213.410, F.A.C.; and, 40 CFR 761.20(e)(3)] {Permitting Note: 40 CFR 761.20, dated March 18, 1996, defines “quantifiable level” of PCBs as greater than or equal to 2 parts per million.} Comments: The test was supposed it be performed using No. 6 fuel oil. Note: On 7/24/07 I informed Erika Tuchbaum that the test results submitted did not indicate the grade of fuel oil used during testing. I pointed out that permit condition no. A 24 states that fuel oil No. 6 shall be used during testing. I also pointed out that the certificates of Analysis do not indicate the type of fuel analyzed. Ms Tuchbaum committed to providing the information before Friday July 27th, 2007. Update: The fuel oil type used during the stack test was No. 6 per the COA attached to the test results in Appendix A: Facility Operating Data. ###### Emission Limitations and Standards A.5. Visible Emissions. Visible emissions shall not exceed 40 percent opacity. [Rules 62-296.405(1)(a) and 62-296.702(2)(b), F.A.C.; and, OGC Order Nos. 86-1577, 87-1261, & 96-A-01] A.6. Visible Emissions - Soot Blowing and Load Change. Visible emissions resulting from boiler cleaning (soot blowing) and load change shall be permitted provided the duration of such excess emissions shall not exceed 3 hours in any 24-hour period and visible emissions shall not exceed 60 percent opacity, and providing (1) best operational practices to minimize emissions are adhered to and (2) the duration of the excess emissions shall be minimized. A load change occurs when the operational capacity of a unit is in the 10 percent to 100 percent capacity range, other than startup or shutdown, which exceeds 10 percent of the unit’s rated capacity and which occurs at a rate of 0.5 percent per minute or more. Visible emissions above 60 percent opacity shall be allowed for not more than 4, six (6) -minute periods, during the 3-hour period of excess emissions allowed under this subparagraph, for boiler cleaning and load changes, at units which have installed and are operating, or have committed to install or operate, continuous opacity monitors. Particulate matter emissions shall not exceed an average of 0.3 lb. per million Btu heat input during the 3-hour period of excess emissions allowed by this subparagraph. [Rules 62-210.700(3) and 62-296.702(2)(b), F.A.C.] A.19. Visible emissions. The test method for visible emissions shall be: a. E.U. ID Nos. -001, -002 and -003 EPA Method 9, incorporated in Chapter 62-297, F.A.C. b. E.U. ID No. -001 Continuous opacity monitor. [Rule 62-296.702(3)(a), F.A.C.; and, AO 52-233149] Comments: An AQD Method 9 VE test was performed during this site visit  Yes or □ No. See report by Mike Thomas for details regarding the opacity test. A.7. Particulate Matter. Particulate matter emissions during steady state operations shall not exceed the following, as measured by applicable compliance methods (see specific condition A.20.): E.U. ID No.; lb/MMBTUs heat input; lb/ hr; Tons per Year. -003; 0.1; 221.1; 968.6. [Rules 62-296.405(1)(b), 62-296.700(4)(b) and 62-296.702(2)(a), F.A.C.] Comments: The last annual compliance test, conducted on 9/26/06 showed emission of 0.0103 lbs/MMBtu. The Results for this year pending submittal and review. The test results for particulate matter and opacity are due lot be submitted no later than 3 July 2007. A.8. Particulate Matter - Soot Blowing and Load Change. Particulate matter emissions shall not exceed an average of the following during the 3-hours in any 24-hour period of excess emissions allowed for boiler cleaning (soot blowing) and load change. E.U. ID No.; lb/MMBTUs heat input; lb/ hr. -003; 0.3; 663.3. [Rules 62-210.700(3) and 62-296.700(4)(b), F.A.C.] Comments: The last annual compliance test, conducted on 9/26/06 showed emission of 0.0499 lbs/MMBtu. The test results for particulate matter and opacity are due lot be submitted no later than 3 July 2007. A.9. Sulfur Dioxide. When burning liquid fuel, sulfur dioxide emissions shall not exceed 2.75 pounds per million Btu heat input, as measured by applicable compliance methods. [Rule 62-296.405(1)(c)1.j., F.A.C.] A.17. Sulfur Dioxide. The permittee elected to demonstrate compliance by accepting a liquid fuel sulfur limit that will be verified with a fuel analysis provided by the vendor or the permittee upon each fuel delivery. This protocol is allowed because the emissions unit does not have an operating flue gas desulphurization device. See specific conditions A.10., A.21. and A.22. [Rule 62-296.405(1)(f)1.b., F.A.C.] A.21. Sulfur Dioxide. The test methods for sulfur dioxide emissions shall be EPA Methods 6, 6A, 6B, or 6C, incorporated by reference in Chapter 62-297, F.A.C. Fuel sampling and analysis may be used as an alternate sampling procedure if such a procedure is incorporated into the operation permit for the emissions unit. If the emissions unit obtains an alternate procedure under the provisions of Rule 62-297.620, F.A.C., the procedure shall become a condition of the emissions unit’s permit. The Department will retain the authority to require EPA Method 6 or 6C if it has reason to believe that exceedences of the sulfur dioxide emissions limiting standard are occurring. Results of an approved fuel sampling and analysis program shall have the same effect as EPA Method 6 test results for purposes of demonstrating compliance or noncompliance with sulfur dioxide standards. The permittee may use the EPA test methods, referenced above, to demonstrate compliance; however, as an alternate sampling procedure authorized by permit, the permittee elected to demonstrate compliance by accepting a liquid fuel sulfur limit that will be verified with a fuel analysis provided by the vendor or the permittee upon each fuel delivery. See specific conditions A.10. and A.22. [Rules 62-213.440, 62-296.405(1)(e)3. and 62-297.401, F.A.C.; and, AO 52-216412, AO 52-216413 & AO 52-233149] Comments: The last annual compliance test, conducted on 9/26/06 showed emission of 2.42 lbsSO2 /MMBtu. The Results for this year pending submittal and review. This year’s test is required to be submitted by 3 July 2007. A.10. Sulfur Dioxide - Sulfur Content. The new No. 6 fuel oil sulfur content shall not exceed 2.5 percent, by weight. The sulfur content of the on-specification used oil shall not exceed 2.5 percent by weight. See specific condition A.22. [Rule 62-296.405(1)(e)3., F.A.C.; and, AO 52-216412, AO 52-216413 & AO 52-233149] Comments: The highest reported sulfur content was 1.51% by weight for the month of February 2007. Reviewed records for the months of October 2006, and February 2007. A.11. “On-Specification” Used Oil. Only “on-specification” used oil shall be fired in these units. The quantity of on-specification used oil fired in emissions units -001, -002 and -003 shall not exceed a total of 14.85 million gallons per consecutive 12-month period and 2.475 million gallons per month. “On-specification” used oil is defined as used oil that meets the 40 CFR 279 (Standards for the Management of Used Oil) specifications listed below. Used oil that does not meet all of the following specifications is considered “off-specification” oil and shall not be fired. CONSTITUENT / PROPERTY * ALLOWABLE LEVEL Arsenic 5 ppm maximum Cadmium 2 ppm maximum Chromium 10 ppm maximum Lead 100 ppm maximum Total Halogens 1000 ppm maximum Flash Point 100°F minimum PCBs less than 50 ppm** * As determined by approved methods specified in EPA Publication SW-846 (Test Methods for Evaluating Solid Waste, Physical/Chemical Methods). ** Used oil shall not be blended to meet this requirement. [40 CFR 279.11; 40 CFR 761.20; and, AO 52-216412, AO 52-216413 & AO 52-233149] Comments: The highest reported use of on-specification used oil was 780 gallons per consecutive 12-month period, at the end of the month of December 2006. A.12. “On-Specification” Used Oil. Before accepting from each marketer the first shipment of on-specification used oil with a PCB concentration above the detectable level, the permittee shall provide each marketer with a one-time written and signed notice certifying that the permittee will burn the used oil in a qualified combustion device. The notice must state that EPA or a RCRA-delegated state agency has been given a description of the used oil management activities at the facility and that an industrial boiler or furnace will be used to burn the used oil with PCB concentrations above the detectable level. The description of the used oil management activities shall be submitted to the Administrator, Hazardous Waste Regulation Section, Florida Department of Environmental Protection, 2600 Blair Stone Road, Tallahassee, Florida 32399-2400. [40 CFR 279.61 and 40 CFR 761.20(e)(3)(ii)] Comments: Progress Energy no longer burns On-specification Used Oil Nil. 5 from outside sources. The on-spec Used oil No. 5 that Progress Energy combusted was generated at its facility and was tested to ensure that it met the requirements of On-spec Used oil No. 5. A.13. “On-Specification” Used Oil. Each shipment or on-site generated batch of used oil shall be sampled and analyzed for the constituents listed in specific condition A.11. A claim that the used oil does not contain quantifiable levels of PCBs must be documented by analysis or other information. The first person making the claim that the used oil does not contain PCBs is responsible for furnishing the documentation. The documentation can be tests, personal or special knowledge of the source and composition of the used oil, or a certification from the person generating the used oil claiming that the used oil contains no detectable PCBs. [40 CFR 761.20(e)(2); and, Rule 62-4.070(3), F.A.C.] Comments: Progress Energy certifies its own On spec Used Oil No 5 by testing it in its own labs, including testing to verify that it doesn’t contain quantifiable levels of PCBs. Excess Emissions {Permitting note: The Excess Emissions Rule at Rule 62-210.700, F.A.C., cannot vary any requirement of a NSPS or NESHAP provision.} A.14. Excess emissions resulting from malfunction shall be permitted provided that best operational practices to minimize emissions are adhered to and the duration of excess emissions shall be minimized but in no case exceed two hours in any 24-hour period unless specifically authorized by the Department for longer duration. [Rule 62-210.700(1), F.A.C.] Comments: Progress Energy submitted its quarterly excess emissions reports for the last 12 months which Showed that it was in compliance with permit condition A 14 above. A.15. Excess emissions resulting from startup or shutdown shall be permitted provided that best operational practices to minimize emissions are adhered to and the duration of excess emissions shall be minimized. [Rule 62-210.700(2), F.A.C.] A.16. Excess emissions which are caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure which may reasonably be prevented during startup, shutdown or malfunction shall be prohibited. [Rule 62-210.700(4), F.A.C.] Comments: Review of the Quarterly Excess Emissions Reports submitted revealed that Progress Energy was applying Best Operational Practices to minimize excess emissions. A.18. Determination of Process Variables. (a) Required Equipment. The owner or operator of an emissions unit for which compliance tests are required shall install, operate, and maintain equipment or instruments necessary to determine process variables, such as process weight input or heat input, when such data are needed in conjunction with emissions data to determine the compliance of the emissions unit with applicable emission limiting standards. (b) Accuracy of Equipment. Equipment or instruments used to directly or indirectly determine process variables, including devices such as belt scales, weight hoppers, flow meters, and tank scales, shall be calibrated and adjusted to indicate the true value of the parameter being measured with sufficient accuracy to allow the applicable process variable to be determined within 10% of its true value. [Rule 62-297.310(5), F.A.C.] Comments: Progress Energy Monitors the Steam Unit Process Variables in its control room. Progress Energy has provided statements from the COR1OLIS Flow Meters from the manufacturer that these are calibrated at the factory and are replaced, not calibrated when they cease working. A.20. Particulate Matter. The test methods for particulate emissions shall be EPA Methods 17, 5, 5B, or 5F, incorporated by reference in Chapter 62-297, F.A.C. The minimum sample volume shall be 30 dry standard cubic feet. EPA Method 5 may be used with filter temperature no more than 320 degrees Fahrenheit. For EPA Method 17, stack temperature shall be less than 375 degrees Fahrenheit. The owner or operator may use EPA Method 5 to demonstrate compliance. EPA Method 3 or 3A with Orsat analysis shall be used when the oxygen based F-factor, computed according to EPA Method 19, is used in lieu of heat input. Acetone wash shall be used with EPA Method 5 or 17. [Rules 62-296.405(1)(e)2., 62-297.401 and 62-296.702(3)(b), F.A.C.] Comments: The consultant, CEM Solutions, used Methods 1, 2, 3a, 4, 9 and 17 to perform the Stack Tests. A.22. The fuel sulfur content, percent by weight, for liquid fuels shall be evaluated using either ASTM D2622-92, ASTM D4294-90, both ASTM D4057-88 and ASTM D129-91, or the latest edition, or ASTM D1552-95 or an equivalent method after Department approval. [Rules 62-213.440, 62-296.405(1)(e)3., 62-296.405(1)(f)1.b. and 62-297.440, F.A.C.] Comments: The COAs revealed that Progress Energy used Method ASTM 1552 for determining sulfur. A.23. Required Number of Test Runs. For mass emission limitations, a compliance test shall consist of three complete and separate determinations of the total air pollutant emission rate through the test section of the stack or duct and three complete and separate determinations of any applicable process variables corresponding to the three distinct time periods during which the stack emission rate was measured provided, however, that three complete and separate determinations shall not be required if the process variables are not subject to variation during a compliance test, or if three determinations are not necessary in order to calculate the unit's emission rate. The three required test runs shall be completed within one consecutive five day period. In the event that a sample is lost or one of the three runs must be discontinued because of circumstances beyond the control of the owner or operator, and a valid third run cannot be obtained within the five day period allowed for the test, the Secretary or his or her designee may accept the results of the two complete runs as proof of compliance, provided that the arithmetic mean of the results of the two complete runs is at least 20 percent below the allowable emission limiting standards. [Rule 62-297.310(1), F.A.C.] Comments: A QD observed one soot run and me non-soot run. The consultant performed 3 soot runs and 3 non-soot runs, per the stack test report submitted. A.2. Emissions Unit Operating Rate Limitation After Testing. See specific condition A.24. [Rule 62-297.310(2), F.A.C.] AND A.24. Operating Rate During Testing. Testing of emissions shall be conducted while firing new No. 6 fuel oil or new No. 6 fuel oil/on-specification used oil with the emissions unit operation at permitted capacity, which is defined as 90 to 100 percent of the maximum operation rate allowed by the permit. If it is impracticable to test at permitted capacity, an emissions unit may be tested at less than the minimum permitted capacity; in this case, subsequent emissions unit operation is limited to 110 percent of the test load until a new test is conducted. Once the emissions unit is so limited, operation at higher capacities is allowed for no more than 15 consecutive days for the purpose of additional compliance testing to regain the authority to operate at the permitted capacity. [Rules 62-297.310(2) & (2)(b), F.A.C.; and, AO 52-216412, AO 52-216413 & AO 52-233149] Comments: The EU was tested during all 6 runs while operating between 90 to 100% of Capacity. A.27. Required Stack Sampling Facilities. When a mass emissions stack test is required, the permittee shall comply with the requirements contained in Appendix SS-1, Stack Sampling Facilities, attached to this permit. [Rule 62-297.310(6), F.A.C.] Comments: The Stack Sampling facilities are in compliance with Rule 62-297.310 A.28. Frequency of Compliance Tests. The following provisions apply only to those emissions units that are subject to an emissions limiting standard for which compliance testing is required. (a) General Compliance Testing. 2. For excess emission limitations for particulate matter specified in Rule 62-210.700, F.A.C., a compliance test shall be conducted annually while the emissions unit is operating under soot blowing conditions in each federal fiscal year during which soot blowing is part of normal emissions unit operation, except that such test shall not be required in any federal fiscal year in which a fossil fuel steam generator does not burn liquid for more than 400 hours other than during startup. 3. The owner or operator of an emissions unit that is subject to any emission limiting standard shall conduct a compliance test that demonstrates compliance with the applicable emission limiting standard prior to obtaining a renewed operation permit. Emissions units that are required to conduct an annual compliance test may submit the most recent annual compliance test to satisfy the requirements of this provision. In renewing an air operation permit pursuant to Rule 62-210.300(2)(a)3.b., c., or d., F.A.C., the Department shall not require submission of emission compliance test results for any emissions unit that, during the year prior to renewal: a. Did not operate; or b. In the case of a fuel burning emissions unit, burned liquid fuel for a total of no more than 400 hours. 4. During each federal fiscal year (October 1 - September 30), unless otherwise specified by rule, order, or permit, the owner or operator of each emissions unit shall have a formal compliance test conducted for: a. Visible emissions, if there is an applicable standard; b. Each of the following pollutants, if there is an applicable standard, and if the emissions unit emits or has the potential to emit: 5 tons per year or more of lead or lead compounds measured as elemental lead; 30 tons per year or more of acrylonitrile; or 100 tons per year or more of any other regulated air pollutant; and c. Each NESHAP pollutant, if there is an applicable emission standard. 5. An annual compliance test for particulate matter emissions shall not be required for any fuel burning emissions unit that, in a federal fiscal year, does not burn liquid fuel, other than during startup, for a total of more than 400 hours. 9. The owner or operator shall notify the PCDEM, at least 15 days prior to the date on which each formal compliance test is to begin, of the date, time, and place of each such test, and the test contact person who will be responsible for coordinating and having such test conducted for the owner or operator. (b) Special Compliance Tests. When the PCDEM, after investigation, has good reason (such as complaints, increased visible emissions or questionable maintenance of control equipment) to believe that any applicable emission standard contained in a Department rule or in a permit issued pursuant to those rules is being violated, it may require the owner or operator of the emissions unit to conduct compliance tests which identify the nature and quantity of pollutant emissions from the emissions unit and to provide a report on the results of said tests to the PCDEM. (c) Waiver of Compliance Test Requirements. If the owner or operator of an emissions unit that is subject to a compliance test requirement demonstrates to the Department, pursuant to the procedure established in Rule 62-297.620, F.A.C., that the compliance of the emissions unit with an applicable weight emission limiting standard can be adequately determined by means other than the designated test procedure, such as specifying a surrogate standard of no visible emissions for particulate matter sources equipped with a bag house or specifying a fuel analysis for sulfur dioxide emissions, the Department shall waive the compliance test requirements for such emissions units and order that the alternate means of determining compliance be used, provided, however, the provisions of Rule 62-297.310(7)(b), F.A.C., shall apply. [Rule 62-297.310(7), F.A.C.; and, SIP approved] Comments: The tests are required of this EU because it does perform soot blowing and there is an applicable VE Standard. A.29. By this permit, annual emissions compliance testing for visible emissions is not required for these emissions units while burning: a. only gaseous fuel(s); or b. gaseous fuel(s) in combination with any amount of liquid fuel(s) for less than 400 hours per year; or c. only liquid fuel(s) for less than 400 hours per year. [Rule 62-297.310(7)(a)4., F.A.C.] A.30. Annual and permit renewal compliance testing for particulate matter emissions is not required for these emissions units while burning: a. only gaseous fuel(s); or b. gaseous fuel(s) in combination with any amount of liquid fuel(s) for less than 400 hours per year; or c. only liquid fuel(s) for less than 400 hours per year. [Rules 62-297.310(7)(a)3. & 5., F.A.C.; and, ASP Number 97-B-01.] Comments: The EU combusted fuel oil No. 6 during the year with lesser amounts of fuel oil No. 2 and some of natural gas. Record keeping and Reporting Requirements A.31. In the case of excess emissions resulting from malfunctions, each owner or operator shall notify the PCDEM in accordance with Rule 62-4.130, F.A.C. A full written report on the malfunctions shall be submitted in a quarterly report, if requested by the PCDEM. [Rule 62-10.700( 6), F.A.C.] A.32. Submit to the PCDEM a written report of emissions in excess of emission limiting standards as set forth in Rule 62-296.405(1), F.A.C., for each calendar quarter. The nature and cause of the excess emissions shall be explained. This report does not relieve the owner or operator of the legal liability for violations. All recorded data shall be maintained on file by the Source for a period of five years. [Rules 62-213.440 and 62-296.405(1)(g), F.A.C.] Comments: Progress Energy submitted its required quarterly excess emissions reports for the past 12 months. The department, however, did not request full written reports. A.33. Test Reports. (a) The owner or operator of an emissions unit for which a compliance test is required shall file a report with the PCDEM on the results of each such test. (b) The required test report shall be filed with the PCDEM as soon as practical but no later than 45 days after the last sampling run of each test is completed. (c) The test report shall provide sufficient detail on the emissions unit tested and the test procedures used to allow the PCDEM to determine if the test was properly conducted and the test results properly computed. As a minimum, the test report, other than for an EPA or DEP Method 9 test, shall provide the following information: 1. The type, location, and designation of the emissions unit tested. 2. The facility at which the emissions unit is located. 3. The owner or operator of the emissions unit. 4. The normal type and amount of fuels used and materials processed, and the types and amounts of fuels used and material processed during each test run. 5. The means, raw data and computations used to determine the amount of fuels used and materials processed, if necessary to determine compliance with an applicable emission limiting standard. 6. The type of air pollution control devices installed on the emissions unit, their general condition, their normal operating parameters (pressure drops, total operating current and GPM scrubber water), and their operating parameters during each test run. 7. A sketch of the duct within 8 stack diameters upstream and 2 stack diameters downstream of the sampling ports, including the distance to any upstream and downstream bends or other flow disturbances. 8. The date, starting time and duration of each sampling run. 9. The test procedures used, including any alternative procedures authorized pursuant to Rule 62-297.620, F.A.C. Where optional procedures are authorized in this chapter, indicate which option was used. 10. The number of points sampled and configuration and location of the sampling plane. 11. For each sampling point for each run, the dry gas meter reading, velocity head, pressure drop across the stack, temperatures, average meter temperatures and sample time per point. 12. The type, manufacturer and configuration of the sampling equipment used. 13. Data related to the required calibration of the test equipment. 14. Data on the identification, processing and weights of all filters used. 15. Data on the types and amounts of any chemical solutions used. 16. Data on the amount of pollutant collected from each sampling probe, the filters, and the impingers, are reported separately for the compliance test. 17. The names of individuals who furnished the process variable data, conducted the test, analyzed the samples and prepared the report. 18. All measured and calculated data required to be determined by each applicable test procedure for each run. 19. The detailed calculations for one run that relate the collected data to the calculated emission rate. 20. The applicable emission standard, and the resulting maximum allowable emission rate for the emissions unit, plus the test result in the same form and unit of measure. 21. A certification that, to the knowledge of the owner or his authorized agent, all data submitted is true and correct. When a compliance test is conducted for the Department or its agent, the person who conducts the test shall provide the certification with respect to the test procedures used. The owner or his authorized agent shall certify that all data required and provided to the person conducting the test are true and correct to his knowledge.2 Comments: The test reports for EUs 003 and 002 were submitted on June 25th, 2007. However, the reports did not contain the detailed calculations of as least one complete run, per 62-297.310 (8) 19 at the time of submittal. Mr. Scott Milsaps from Progress Energy committed to getting them in to AQD within 24 of my phone call on 7/17/0. Update: The detailed calculations were received on 7/18/07 as email from Mr. Milsaps and are attached to the corresponding results previously submitted for each emission unit. A.34. Not federally enforceable. Special Recordkeeping Requirements: The owner or operator shall obtain, make, and keep the following records related to the use of used oil: (1) The gallons of on-specification used oil burned each month. (This record shall be completed no later than the fifteenth day of the succeeding month.) (2) The total gallons of on-specification used oil burned in the preceding calendar year. (3) The name and address of all marketers delivering used oil to the facility. (4) Copies of the marketer certifications, if obtained, and any supporting information. (5) Documentation that the used oil contains less than 2 ppm PCBs, if claimed, including the name and address of the person making the claim. (6) Results of the analyses required above. (7) A copy of the notice to EPA and a copy of the one-time written notice provided to each marketer. These records shall be re The on-specification used oil corded in a permanent form suitable for inspection by the PCDEM upon request, and shall be retained for at least a five year period. [40 CFR 279.61; 40 The facility had records on the internal accumulations of the 780 gallons of nosed oil during the year at-this own CFR 761.20(e); and, Rule 62-213.440(1)(b)2.b., F.A.C.] Comments: The facility had records that showed the accumulation of the 780 gallons of used oil that were combusted in the year 2006. All of the used oil was generated by Progress Energy itself. A.35. The permittee shall include in the “Annual Operating Report for Air Pollutant Emitting Facility” a statement of the total quantity of on-specification used oil fired during the calendar year. [Rule 62-4.070(3), F.A.C.; and, AO 52-216412, AO 52-216413 & AO 52-233149] Comments: The facility included a statement of the total quantity of on-specification used ail fired during the calendar year in the steam units. A.36. Compliance with the oil sulfur content and the sulfur dioxide emissions limitations of specific conditions A.9. and A.10. shall be documented by the permittee through submittal of quarterly reports of the Bartow Plant monthly average fuel oil sulfur content, heat content and the resulting sulfur dioxide emission rate in pounds per million Btu heat input. These quarterly reports shall be submitted to PCDEM within 30 days of the end of each calendar quarter. [Rule 62-4.070(3), F.A.C.; and, AO 52-216412, AO 52-216413 & AO 52-233149] Comments: The facility submitted the quarterly reports due in 2006 and prior to the test on May 16th, 2007 had submitted the first quarterly report due for 2007. A.37. Not Federally Enforceable. Submit to the Air Section of PCDEM each calendar year on or before March 1, a completed “Annual Operating Report for Air Pollutant Emitting Facility” form for the preceding calendar year. Until further notice by the Department the permittee shall calculate particulate matter emissions by multiplying the particulate matter stack test results by the hours of operation. Other annual emissions shall be determined by multiplying the annual fuel use by the following emissions factors: E.U. ID No. -003. Pollutant; No. 6 fuel oil (lb/1000 gal); Natural Gas (lb/MMcf). SO2; 157(S); 0.6. CO; 5; 5. NOX; 42; 550. VOC; 0.76; 1.4. [AO 52-216412, AO 52-216413 & AO 52-233149] Comments: The facility submitted the 2006 AOR with SO2 and NOx emission factors derived from Continuous Emissions Monitoring; VOC and CO from published sources and PM from actual on-site stack tests performed during the previous year. A.38. COMS for Periodic Monitoring. The owner or operator is required to install continuous opacity monitoring systems (COMS) pursuant to 40 CFR Part 75. The owner or operator shall maintain and operate COMS and shall make and maintain records of opacity measured by the COMS, for purposes of periodic monitoring. [Rule 62-213.440, F.A.C.] Comments: The EU has COMS installed and documentation provided during the year indicates that they are maintained as required. Miscellaneous Requirements A.39. Process Parameters. E.U. ID No. -003. Heat Input Rate; 2,266 MMBTUs/hr (maximum). Fuel; New No. 6 fuel oil with a sulfur content of 2.5%, by weight (maximum) and on-specification used oil with a sulfur content of 2.5%, by weight (maximum) (also natural gas when available). Fuel Firing Rate; 14,742 gal/hr (351 BBL/hr) new No. 6 fuel oil and/or on-specification used oil, 2.2 MMcf/hr natural gas (maximum). Ash Content; As sampled. Steam Temperature; 1,000°F. Steam Pressure; 2,050 psi. Steam Flow Rate; 1,423,500 lb/hr. Stack Height; 300 ft. Boiler Manufacturer; Combustion Engineering. Burner Arrangement; Tangential fired. Inspection and Maintenance Program. (a) Scheduled during major outages: Boilers, controls, auxiliaries, burners and duct work are to be inspected and repaired as necessary. All parts are to be inspected, cleaned and replaced as necessary. (b) Scheduled during non-peak load periods in Spring and Fall: This schedule is affected by forced outage requirements. (c) The following operating parameters are to be continuously monitored and maintained at appropriate levels to produce efficient fuel combustion: 1. fuel flow rate 2. fuel temperature 3. fuel pressure 4. air flow rate 5. steam flow rate 6. steam temperature 7. steam pressure (d) Plant operators are to monitor, adjust and record the following operating parameters at least once per day to assure efficient plant operation: 1. temperatures (superheat, reheat, and fuel) 2. flows (steam, feed water, and fuel) 3. unit load (e) Fuel oil quality is to be checked prior to delivery and a daily sample taken each day the facility is operated for a monthly composite analysis. Fuel oil analysis (by ASTM Methods) is to be analyzed for the following: 1. heat content (Btu/gal) 2. sulfur content (%S by weight) 3. density 4. API gravity Records of inspection, maintenance, and performance parameters shall be retained a minimum of five years and shall be mad available for inspection upon request. [Rule 62-296.700 (6)(d), F.A.C.; and, AO 52-216412, AO 52-216413 & AO 52-233149] Comments: The beginning and ending process parameters for the test performed on 5/16/07 averaged: - fuel flow rate : 300 BBl/Hr of Fuel Oil No. 6 - fuel temperature: 160o F - fuel pressure: 142 PSI - air flow rate: 1,395 KLbs/hour - heat input: 1,989 MMBtu/hr - sulfur content: 1.49 %/wt - density: 9.014 lbs/gal @ 60o F - API gravity: -0.8 deg. API @ 60o F These parameters are in compliance with permit condition No. A. 39. above. A.41. PSD Applicability Report: The permittee shall maintain information demonstrating that the project (1030011-007-AC) did not result in any significant net emissions increase of particulate matter, which is defined in Rule 62-212.400(2)(e), F.A.C., as follows: Net Emissions Increase. A modification to a facility results in a net emissions increase when, for a pollutant regulated under the Act, the sum of all of the contemporaneous creditable increases and decreases in the actual emissions of the facility, including the increase in emissions of the modification itself and any increases and decreases in quantifiable fugitive emissions, is greater than zero. Significant Net Emissions Increase. A significant net emissions increase of a pollutant regulated under the Act is a net emissions increase equal to or greater than the applicable significant emission rate listed in Table 212.400-2, Regulated Air Pollutants – Significant Emission Rates. The permittee shall submit an annual report to the Department of such information for a period of 5 years representative of normal post-change operations of the unit (within the period not longer than 10 years following the change). For an existing electric utility steam-generating unit, actual emissions of the unit following a physical or operational change shall equal the representative actual annual emissions of the unit following the physical or operational change. The following definition of “representative actual annual emissions” found in 40 CFR 52.21(b)(33) is adopted and incorporated by reference in Rule 62-204.800, F.A.C. Representative actual annual emissions means the average rate, in tons per year, at which the source is projected to emit a pollutant for the two-year period after a physical change or change in the method of operation of a unit, (or a different consecutive two-year period within 10 years after that change, where the Administrator determines that such period is more representative of normal source operations), considering the effect any such change will have on increasing or decreasing the hourly emissions rate and on projected capacity utilization. In projecting future emissions the Administrator shall: (i) Consider all relevant information, including but not limited to, historical operational data, the company's own representations, filings with the State or Federal regulatory authorities, and compliance plans under title IV of the Clean Air Act; and (ii) Exclude, in calculating any increase in emissions that results from the particular physical change or change in the method of operation at an electric utility steam generating unit, that portion of the unit's emissions following the change that could have been accommodated during the representative baseline period and is attributable to an increase in projected capacity utilization at the unit that is unrelated to the particular change, including any increased utilization due to the rate of electricity demand growth for the utility system as a whole. Each required annual report shall be submitted to the Department prior to March 1st and shall quantify operations for the previous calendar year(s). [1030011-007-AC] Comments: This project was completed and no emissions increases were reported or observed at the time of installation or since its installation. Acid Rain Provisions A.2. Sulfur dioxide (SO2) allowance allocations requirements for each Acid Rain unit are as follows: E.U. ID No.; EPA ID; Year; 2005; 2006; 2007; 2008; 2009. -003; 03; SO2 allowances, under Table 2 or 3 of 40 CFR Part 73; 5428*; 5428*; 5428*; 5428*; 5428*. *The number of allowances held by an Acid Rain source in a unit account may differ from the number allocated by the USEPA under Table 2 or 3 of 40 CFR 73.7 A.3. Emission Allowances. Emissions from sources subject to the Federal Acid Rain Program (Title IV) shall not exceed any allowances that the source lawfully holds under the Federal Acid Rain Program. Allowances shall not be used to demonstrate compliance with a non-Title IV applicable requirement of the Act. 1. No permit revision shall be required for increases in emissions that are authorized by allowances acquired pursuant to the Federal Acid Rain Program, provided that such increases do not require a permit revision pursuant to Rule 62-213.400(3), F.A.C. 2. No limit shall be placed on the number of allowances held by the source under the Federal Acid Rain Program. 3. Allowances shall be accounted for under the Federal Acid Rain Program. [Rule 62-213.440(1)(c), F.A.C.] Comments: PE used 6,153.9 tons of SO2 allowances in 2006. (they used 725.9 tons from their bank-account to make – up the difference from their permit allowable). A.4. Fast-Track Revisions of Acid Rain Parts. Those Acid Rain sources making a change described at Rule 62- 214.370(4), F.A.C., may request such change as provided in Rule 62-213.413, F.A.C., Fast-Track Revisions of Acid Rain Parts. [Rules 62-213.413 and 62-214.370(4), F.A.C.] Comments: There are no Fast-track Revisions of Acid Rain Parts on record for Progress Energy. |
| ` |  |  | #### Valid Permit [Rule 62-210.300] |
|  |  |  | #### Changes to Facility/emission unit [Rule 62-210.300] Does the emission unit description above match what the facility is operating (Number of emission units or point’s) Yes No Comments: |

|  |  | . Other: |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Pollution Prevention Activities - P2 Handouts Provided: P2 Brochure; P2 Manual; P2 Checklist - Have any emissions reductions occurred Yes / No Chemical Substitution; Equipment Changes; Process Changes Chemical/Material Reuse; On-site Recycling; Other: Comments: There were no activities reported or observed that could be construed as P2. |  |  |  |  |  |  |  |
| Closing Conference: In the closing conference, I informed Erika Tuchbaum that The Emission Unit was in compliance pending submittal of acceptable stack test results. |  |  |  |  |  |  |  |
| Inspector(s): Jose Rodriguez, Pinellas County, Air Quality Division |  |  |  |  |  |  |  |
| Signature(s): Date: |  |  |  |  |  |  | Date: July 23rd, 2007. |
|  | # ACCESS? |  |  | # EASIIR |  |  |  |

/tmp/in/input.doc