| 1030011 004 57518 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| FACILITY: Progress Energy Florida, Inc. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PERMIT ID: 71 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Florida Power, Bartow Plant |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DISTRICT: Southwest |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ADDRESS: 1601 Weedon Island Drive |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CONTACT PHONE: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| St. Petersburg, FL |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 727-826-4130 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ARMS NO: 1030011 004 |  |  |  |  |  |  |  | PERMIT NO: |  |  |  |  |  |  |  |  |  |  |  |  | EXPIRATION DATE: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | 1030011-009-AV |  |  |  |  |  |  |  |  |  |  |  |  | 12/31/09 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| EMISSION UNIT DESCRIPTION : Pipeline Heater Boiler. The boiler’s maximum heat input rate is 15.5 million Btu per hour firing natural gas, No. 2 fuel oil, or propane |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| INSPECTION DATE: |  |  |  |  |  |  | ARMS INSPECTION TYPE: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | COMPLIANCE STATUS: |  |  |  |  |  |  |  |  |  |  |  |  |
|  | May 16, 2007 |  |  |  |  |  |  |  |  |  | INS1 |  |  | INS2 |  |  | INS3 |  |  | FUI |  |  |  |  |  | IN |  |  | MNC |  |  |  |  | SNC |  |
| INSPECTION TYPE: |  |  |  |  | Initial |  |  |  |  |  |  | Re-inspection |  |  |  |  |  | Complaint |  |  |  |  |  |  | Drive-by |  |  |  |  |  | Quarterly |  |  |  |  |
|  |  |  | A. General Review: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1. |  | Permit File Review |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  |  |  | No |
|  |  | Comments: On May 9th, 2007 the AQD e -mailed Progress Energy details of information that would be required for the inspections during stack testing of Emission Units 001, 002, and 003. Some of the information would be generated during the testing and some of it would have to wait until then. However, other information, such as certificates of analysis and EU # 001 ESP parameters, could be obtained prior to the arrival of AQD personnel. The testing was performed by CEM Solutions, headed by Jeremy Johnson. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2. |  | Introduction and Entry |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  |  |  | No |
|  |  | Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3. |  | Is the Responsible Official/Authorized Representative still: Tom Lawery? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  |  |  | No |
|  |  | Comments: The R.O. is Rufus Jackson. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4. |  | Is the facility contact still: Scott Stenger, Steve Ryan, Dave Meyer? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  |  |  | No |
|  |  | Comments: The new contacts are Therese Sanchez and Erika Tuchbaum. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| IN | MNC | SNC | B. Specific Conditions: |
| --- | --- | --- | --- |
|  |  |  | Section II. Facility-wide Conditions. This permit or a copy thereof shall be kept at the work site of the permitted activity. [APPENDIX TV-4, TITLE V CONDITION 12(12)] Comments: The facility contact showed me a copy of the permit. Renewals. Prior to one hundred eighty (180) days before the expiration of a permit issued pursuant to Chapter 62-213, F.A.C., the permittee shall apply for a renewal of a permit using forms incorporated by reference in the specific rule chapter for that kind of permit. [APPENDIX TV-4, TITLE V CONDITION 5] Comments: The permit application is due to be submitted on, or before 7/5/09. I read the permit conditions to the facility contact. 2. General Pollutant Emission Limiting Standards. Objectionable Odor Prohibited. The permittee shall not cause, suffer, allow, or permit the discharge of air pollutants which cause or contribute to an objectionable odor. [Rule 62-296.320(2), F.A.C] Comments: An upwind/downwind survey of the facility was conducted. The observed parameters were: Downwind odor detected- none; Wind direction – East Upwind odor detected-none. 3. General Particulate Emission Limiting Standards. General Visible Emissions Standard - Except for emissions units that are subject to a particulate matter or opacity limit set forth or established by rule and reflected by conditions in this permit, no person shall cause, let, permit, suffer or allow to be discharged into the atmosphere the emissions of air pollutants from any activity, the density of which is equal to or greater than that designated as Number 1 on the Ringelmann Chart (20 percent opacity). EPA Method 9 is the method of compliance pursuant to Chapter 62-297, F.A.C. [Rules 62-296.320(4)(b)1. & 4., F.A.C.] Comments: There were no unconfined emissions from this EU or the facility property on which it is located. 4. Prevention of Accidental Releases (Section 112(r) of CAA). If required by 40 CFR 68, the permittee shall submit to the implementing agency: A. A risk management plan (RMP) when, and if, such requirement becomes applicable; and B. Certification forms and/or RMPs according to the promulgated rule schedule. [40 CFR 68] Comments: An upwind/downwind survey of the facility was conducted. The observed parameters were: Downwind odor detected- none; Wind direction – East Upwind odor detected-none. 7. General Pollutant Emission Limiting Standards. Volatile Organic Compounds (VOC) Emissions or Organic Solvents (OS) Emissions. The permittee shall allow no person to store, pump, handle, process, load, unload or use in any process or installation, volatile organic compounds (VOC) or organic solvents (OS) without applying known and existing vapor emission control devices or systems deemed necessary and ordered by the Department. “Nothing was deemed necessary and ordered at this time.” [Rule 62-296.320(1)(a), F.A.C.] Comments: There were no drums with solvents in the area of this boiler. However, at all other Emission Units where there were solvents, the containers had lids. 8. Emissions of Unconfined Particulate Matter. Pursuant to Rules 62-296.320(4)(c)1., 3. & 4., F.A.C., reasonable precautions to prevent emissions of unconfined particulate matter at this facility include the following requirements (see Condition 57. of APPENDIX TV-4, TITLE V CONDITIONS): The following requirements are “not federally enforceable”: a. Maintenance of paved areas as needed; b. Regular mowing of grass and care of vegetation; and, c. Limiting access to plant property by unnecessary vehicles. [Rule 62-296.320(4)(c)2., F.A.C.; and, proposed by the applicant in the initial Title V permit application received June 14, 1996] Comments: There is a lot of on-going construction activity at Progress Energy. To keep fugitive dust emissions to a minimum, Progress Energy has a water truck with which the roads on the premises were being watered continuously. 10. Statement of Compliance. The annual statement of compliance pursuant to Rule 62-213.440(3)(a)2., F.A.C., shall be submitted to the Department and EPA within 60 (sixty) days after the end of the calendar year using DEP Form No. 62-213.900(7), F.A.C. [Rules 62-213.440(3) and 62-213.900, F.A.C.] {Permitting Note: This condition implements the requirements of Rules 62-213.440(3)(a)2. & 3., F.A.C. (see Condition 51. of APPENDIX TV-4, TITLE V CONDITIONS)} Comments: The Statement of compliance of calendar year 2006 was submitted on Feb 8th, 2007 Essential Potential to Emit (PTE) Parameters B.1. Permitted Capacity. The maximum operation heat input rate is 15.5 million Btu per hour. [Rules 62-4.160(2), 62-210.200(PTE) and 62-296.406, F.A.C.] {Permitting note: The heat input limitations have been placed in each permit to identify the capacity of each unit for the purposes of confirming that emissions testing is conducted within 90 to 100 percent of the unit’s rated capacity (or to limit future operation to 110 percent of the test load), to establish appropriate emission limits and to aid in determining future rule applicability. Regular record keeping is not required for heat input. Instead the owner or operator is expected to determine heat input whenever emission testing is required, to demonstrate at what percentage of the rated capacity that the unit was tested. Rule 62-297.310(5), F.A.C., included in the permit, requires measurement of the process variables for emission tests. Such heat input determination may be based on measurements of fuel consumption by various methods including but not limited to fuel flow metering or tank drop measurements, using the heat value of the fuel determined by the fuel vendor or the owner or operator, to calculate average hourly heat input during the test.} Comments: This boiler operated 5,335 hours from May 2006 thru April 2007 (12 mos.) with Natural gas only. It was therefore not required to perform visible emissions (VE) testing nor PM testing per permit condition Nos. B19 and B 20. See the natural gas usage record attached. The Boilers connection to the Fuel Oil No. 2 pipeline was removed 3 year ago. That is based on my observation of the pipeline labeling and connection to the boiler itself. B.3. Methods of Operation. Fuels. This boiler is permitted to fire only the following fuels and at the maximum rates shown: Fuel; Maximum % Sulfur; Maximum MMBtu/hr; Maximum Fuel Usage. Natural Gas; - -; 15.5; 15 Mcf/hr. No. 2 Fuel Oil*; 0.5% by weight; 15.5; 110 gal/hr. Propane; - -; 15.5; 191 gal/hr. * New No. 2 fuel oil only (waste or recycled oil is not allowed) [Rule 62-213.410, F.A.C.; and, AO 52-244478] Comments: The highest MMBTU per hour average was achieved during the month of April 2007 with 13.66 MMBTU/hr. ###### Emission Limitations and Standards B.5. Visible Emissions. Visible emissions shall not exceed 20 percent opacity, except for one two-minute period per hour during which opacity shall not exceed 40 percent. [Rule 62-296.406(1), F.A.C.; and, AO 52-244478] B.6. Visible emissions - Soot Blowing and Load Change. Visible emissions shall not exceed 60 percent opacity during the 3-hours in any 24 hour period of excess emissions allowed for boiler cleaning (soot blowing) and load change. A load change occurs when the operational capacity of a unit is in the 10 percent to 100 percent capacity range, other than startup or shutdown, which exceeds 10 percent of the unit’s rated capacity and which occurs at a rate of 0.5 percent per minute or more. Visible emissions above 60 percent opacity shall be allowed for not more than 4, six (6) minute periods, during the 3-hour period of excess emissions allowed by the subparagraph, for boiler cleaning or load changes, at units which have installed and are operating, or have committed to install and operate, continuous opacity monitors. [Rule 62-210.700(3), F.A.C.] Comments: No visible emissions test was required of this Emission Unit for the 12 month period from May of 2006 to April of 2007 per the fuel type used, i.e. Natural Gas. B.7. Sulfur Dioxide - Sulfur Content. The new No. 2 fuel oil sulfur content shall not exceed 0.5 percent, by weight. See specific condition B.15. [Rule 62-296.406(3), F.A.C.; and, AO 52-244478] Comments: This EU no longer uses Fuel Oil No. 2. ###### Excess Emissions {Permitting note: The Excess Emissions Rule at Rule 62-210.700, F.A.C., cannot vary any requirement of a NSPS or NESHAP provision.} B.8. Excess emissions resulting from malfunction shall be permitted provided that best operational practices to minimize emissions are adhered to and the duration of excess emissions shall be minimized but in no case exceed two hours in any 24 hour period unless specifically authorized by the Department for longer duration. [Rule 62-210.700(1), F.A.C.] B.9. Excess emissions resulting from startup or shutdown shall be permitted provided that best operational practices to minimize emissions are adhered to and the duration of excess emissions shall be minimized. [Rule 62-210.700(2), F.A.C.] B.10. Excess emissions which are caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure which may reasonably be prevented during startup, shutdown or malfunction shall be prohibited. [Rule 62-210.700(4), F.A.C.] ###### Record keeping and Reporting Requirements B.21. In the case of excess emissions resulting from malfunctions, each owner or operator shall notify PCDEM in accordance with Rule 62-4.130, F.A.C. A full written report on the malfunctions shall be submitted in a quarterly report, if requested by PCDEM. [Rule 62-210.700(6), F.A.C.] Comments: There were no excess emissions from this emission unit. ###### Monitoring of Operations B.11. Determination of Process Variables. (a) Required Equipment. The owner or operator of an emissions unit for which compliance tests are required shall install, operate, and maintain equipment or instruments necessary to determine process variables, such as process weight input or heat input, when such data are needed in conjunction with emissions data to determine the compliance of the emissions unit with applicable emission limiting standards. (b) Accuracy of Equipment. Equipment or instruments used to directly or indirectly determine process variables, including devices such as belt scales, weight hoppers, flow meters, and tank scales, shall be calibrated and adjusted to indicate the true value of the parameter being measured with sufficient accuracy to allow the applicable process variable to be determined within 10% of its true value. [Rule 62-297.310(5), F.A.C.] Comments: The facility has provided statements form the manufacturer of the flow meters that these are calibrated at the factory and that that is all that’s needed. B.14. Sulfur Dioxide. The permittee elected to demonstrate compliance by accepting a liquid fuel sulfur limit that will be verified with a fuel analysis provided by the vendor or the permittee upon each fuel delivery. This protocol is allowed because the emissions unit does not have an operating flue gas desulfurization device. See specific conditions B.7. and B.15. [Rule 62-296.406(3), F.A.C.] B.15. The fuel sulfur content, percent by weight, for liquid fuels shall be evaluated using either ASTM D2622-92, ASTM D4294-90, both ASTM D4057-88 and ASTM D129-91, or the latest edition, or ASTM D1552-95 or an equivalent method after Department approval. [Rules 62-213.440 and 62-297.440, F.A.C.] Comments: The EU uses NG as fuel whose sulfur content is 0.05 %. B.2. Emissions Unit Operating Rate Limitation After Testing. See specific condition B.16. [Rule 62-297.310(2), F.A.C.] AND B.16. Operating Rate During Testing. Testing of emissions shall be conducted with the emissions unit operation at permitted capacity, which is defined as 90 to 100 percent of the maximum operation rate allowed by the permit. If it is impracticable to test at permitted capacity, an emissions unit may be tested at less than the minimum permitted capacity; in this case, subsequent emissions unit operation is limited to 110 percent of the test load until a new test is conducted. Once the emissions unit is so limited, operation at higher capacities is allowed for no more than 15 consecutive days for the purpose of additional compliance testing to regain the authority to operate at the permitted capacity. [Rules 62-297.310(2) & (2)(b), F.A.C.] B.17. Applicable Test Procedures. (a) Required Sampling Time. 1. Unless otherwise specified in the applicable rule, the required sampling time for each test run shall be no less than one hour and no greater than four hours, and the sampling time at each sampling point shall be of equal intervals of at least two minutes. 2. Opacity Compliance Tests. When either EPA Method 9 or DEP Method 9 is specified as the applicable opacity test method, the required minimum period of observation for a compliance test shall be sixty (60) minutes for emissions units which emit or have the potential to emit 100 tons per year or more of particulate matter, and thirty (30) minutes for emissions units which have potential emissions less than 100 tons per year of particulate matter and are not subject to a multiple-valued opacity standard. The opacity test observation period shall include the period during which the highest opacity emissions can reasonably be expected to occur. Exceptions to these requirements are as follows: c. The minimum observation period for opacity tests conducted by employees or agents of the Department to verify the day-to-day continuing compliance of a unit or activity with an applicable opacity standard shall be twelve minutes. [Rule 62-297.310(4), F.A.C.] B.18. Frequency of Compliance Tests. The following provisions apply only to those emissions units that are subject to an emissions limiting standard for which compliance testing is required. (a) General Compliance Testing. 2. For excess emission limitations for particulate matter specified in Rule 62-210.700, F.A.C., a compliance test shall be conducted annually while the emissions unit is operating under soot blowing conditions in each federal fiscal year during which soot blowing is part of normal emissions unit operation, except that such test shall not be required in any federal fiscal year in which a fossil fuel steam generator does not burn liquid for more than 400 hours other than during startup. 3. The owner or operator of an emissions unit that is subject to any emission limiting standard shall conduct a compliance test that demonstrates compliance with the applicable emission limiting standard prior to obtaining a renewed operation permit. Emissions units that are required to conduct an annual compliance test may submit the most recent annual compliance test to satisfy the requirements of this provision. In renewing an air operation permit pursuant to Rule 62-210.300(2)(a)3.b., c., or d., F.A.C., the Department shall not require submission of emission compliance test results for any emissions unit that, during the year prior to renewal: a. Did not operate; or b. In the case of a fuel burning emissions unit, burned liquid fuel for a total of no more than 400 hours. 4. During each federal fiscal year (October 1 - September 30), unless otherwise specified by rule, order, or permit, the owner or operator of each emissions unit shall have a formal compliance test conducted for: a. Visible emissions, if there is an applicable standard; b. Each of the following pollutants, if there is an applicable standard, and if the emissions unit emits or has the potential to emit: 5 tons per year or more of lead or lead compounds measured as elemental lead; 30 tons per year or more of acrylonitrile; or 100 tons per year or more of any other regulated air pollutant; and c. Each NESHAP pollutant, if there is an applicable emission standard. 5. An annual compliance test for particulate matter emissions shall not be required for any fuel burning emissions unit that, in a federal fiscal year, does not burn liquid fuel, other than during startup, for a total of more than 400 hours. 9. The owner or operator shall notify the PCDEM, at least 15 days prior to the date on which each formal compliance test is to begin, of the date, time, and place of each such test, and the test contact person who will be responsible for coordinating and having such test conducted for the owner or operator. (b) Special Compliance Tests. When the PCDEM, after investigation, has good reason (such as complaints, increased visible emissions or questionable maintenance of control equipment) to believe that any applicable emission standard contained in a Department rule or in a permit issued pursuant to those rules is being violated, it may require the owner or operator of the emissions unit to conduct compliance tests which identify the nature and quantity of pollutant emissions from the emissions unit and to provide a report on the results of said tests to the PCDEM. (c) Waiver of Compliance Test Requirements. If the owner or operator of an emissions unit that is subject to a compliance test requirement demonstrates to the Department, pursuant to the procedure established in Rule 62-297.620, F.A.C., that the compliance of the emissions unit with an applicable weight emission limiting standard can be adequately determined by means other than the designated test procedure, such as specifying a surrogate standard of no visible emissions for particulate matter sources equipped with a bag house or specifying a fuel analysis for sulfur dioxide emissions, the Department shall waive the compliance test requirements for such emissions units and order that the alternate means of determining compliance be used, provided, however, the provisions of Rule 62-297.310(7)(b), F.A.C., shall apply. [Rule 62-297.310(7), F.A.C.; and, SIP approved] B.19. By this permit, annual emissions compliance testing for visible emissions is not required for these emissions units while burning: a. only gaseous fuel(s); or b. gaseous fuel(s) in combination with any amount of liquid fuel(s) for less than 400 hours per year; or c. only liquid fuel(s) for less than 400 hours per year. [Rule 62-297.310(7)(a)4., F.A.C.] B.20. Annual and permit renewal compliance testing for particulate matter emissions is not required for these emissions units while burning: a. only gaseous fuel(s); or b. gaseous fuel(s) in combination with any amount of liquid fuel(s) for less than 400 hours per year; or c. only liquid fuel(s) for less than 400 hours per year. [Rules 62-297.310(7)(a)3. & 5., F.A.C.; and, ASP Number 97-B-01.] Comments: No visible emissions test was required of this Emission Unit for the 12 month period from May of 2006 to April of 2007 per the fuel type used, i.e. Natural Gas. B.22. All recorded data shall be maintained on file by the Source for a period of five years. [Rule 62-213.440, F.A.C.] Comments: The facility has the records for the last 6 years. B.23. Test Reports. (a) The owner or operator of an emissions unit for which a compliance test is required shall file a report with the PCDEM on the results of each such test. (b) The required test report shall be filed with the PCDEM as soon as practical but no later than 45 days after the last sampling run of each test is completed. (c) The test report shall provide sufficient detail on the emissions unit tested and the test procedures used to allow the PCDEM to determine if the test was properly conducted and the test results properly computed. As a minimum, the test report, other than for an EPA or DEP Method 9 test, shall provide the following information: 1. The type, location, and designation of the emissions unit tested. 2. The facility at which the emissions unit is located. 3. The owner or operator of the emissions unit. 4. The normal type and amount of fuels used and materials processed, and the types and amounts of fuels used and material processed during each test run. 5. The means, raw data and computations used to determine the amount of fuels used and materials processed, if necessary to determine compliance with an applicable emission limiting standard. 6. The type of air pollution control devices installed on the emissions unit, their general condition, their normal operating parameters (pressure drops, total operating current and GPM scrubber water), and their operating parameters during each test run. 7. A sketch of the duct within 8 stack diameters upstream and 2 stack diameters downstream of the sampling ports, including the distance to any upstream and downstream bends or other flow disturbances. 8. The date, starting time and duration of each sampling run. 9. The test procedures used, including any alternative procedures authorized pursuant to Rule 62-297.620, F.A.C. Where optional procedures are authorized in this chapter, indicate which option was used. 10. The number of points sampled and configuration and location of the sampling plane. 11. For each sampling point for each run, the dry gas meter reading, velocity head, pressure drop across the stack, temperatures, average meter temperatures and sample time per point. 12. The type, manufacturer and configuration of the sampling equipment used. 13. Data related to the required calibration of the test equipment. 14. Data on the identification, processing and weights of all filters used. 15. Data on the types and amounts of any chemical solutions used. 16. Data on the amount of pollutant collected from each sampling probe, the filters, and the impingers, are reported separately for the compliance test. 17. The names of individuals who furnished the process variable data, conducted the test, analyzed the samples and prepared the report. 18. All measured and calculated data required to be determined by each applicable test procedure for each run. 19. The detailed calculations for one run that relate the collected data to the calculated emission rate. 20. The applicable emission standard, and the resulting maximum allowable emission rate for the emissions unit, plus the test result in the same form and unit of measure. 21. A certification that, to the knowledge of the owner or his authorized agent, all data submitted are true and correct. When a compliance test is conducted for the Department or its agent, the person who conducts the test shall provide the certification with respect to the test procedures used. The owner or his authorized agent shall certify that all data required and provided to the person conducting the test are true and correct to his knowledge. [Rules 62-213.440 and 62-297.310(8), F.A.C.] Comments: No tests were required nor were there any test reports required. |
|  |  |  | #### Valid Permit [Rule 62-210.300] |
|  |  |  | #### Changes to Facility/emission unit [Rule 62-210.300] Does the emission unit description above match what the facility is operating Yes No Comments: |

|  |  | C. Other: |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Pollution Prevention Activities - P2 Handouts Provided: P2 Brochure; P2 Manual; P2 Checklist - Have any emissions reductions occurred Yes / No Chemical Substitution; Equipment Changes; Process Changes Chemical/Material Reuse; On-site Recycling; Other: Comments: There were me recorded reductions of emissions. |  |  |  |  |  |  |  |
| Closing Conference: |  |  |  |  |  |  |  |
| Inspector(s): Jose Rodriguez, Pinellas County, Air Quality Division |  |  |  |  |  |  |  |
| Signature(s): Date: |  |  |  |  |  |  | Date: 8/28/07 |
|  | # ACCESS? |  |  | # EASIIR? |  |  |  |

/tmp/in/input.doc