| 1030095 003 57343 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| FACILITY: Bayfront Medical Center |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PERMIT ID: 2249 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DISTRICT: Southwest |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ADDRESS: 750 5th Avenue South |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CONTACT PHONE: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| St. Petersburg, FL |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 727-893-6825 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ARMS NO: 1030095 003 |  |  |  |  |  |  |  | PERMIT NO: |  |  |  |  |  |  |  |  |  |  |  |  | EXPIRATION DATE: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | 1030095-003-AV |  |  |  |  |  |  |  |  |  |  |  |  | 7/10/06 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| EMISSION UNIT DESCRIPTION : Cleaver Brooks, Model CB 700-300, Serial No. L-90686, Boiler With a Maximum Heat Input Rate of 12.6 MMBTU/hr. and is Subject to 40 CFR 60, Subpart Dc |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| INSPECTION DATE: |  |  |  |  |  |  | ARMS INSPECTION TYPE: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | COMPLIANCE STATUS: |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 26 March 2007 |  |  |  |  |  |  |  |  |  | INS1 |  |  | INS2 |  |  | INS3 |  |  | FUI |  |  |  |  |  | IN |  |  | MNC |  |  |  |  | SNC |  |
| INSPECTION TYPE: |  |  |  |  | Initial |  |  |  |  |  |  | Re-inspection |  |  |  |  |  | Complaint |  |  |  |  |  |  | Drive-by |  |  |  |  |  | Quarterly |  |  |  |  |
|  |  |  | A. General Review: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1. |  | Permit File Review |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  |  |  | No |
|  |  | Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2. |  | Introduction and Entry |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  |  |  | No |
|  |  | Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3. |  | Is the Responsible Official/Authorized Representative still: William A. Christie? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  |  |  | No |
|  |  | Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4. |  | Is the facility contact still: Robert Fairburn? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  |  |  | No |
|  |  | Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| IN | MNC | SNC | B. Specific Conditions: |
| --- | --- | --- | --- |
|              |  |  | - Section II. Facility-wide Conditions. The following conditions apply facility-wide: This permit or a copy thereof shall be kept at the work site of the permitted activity. [APPENDIX TV-3, TITLE V CONDITION 12] Comments: Mr. Fairburn showed me the copy of the permit. 2. General Pollutant Emission Limiting Standards. Objectionable Odor Prohibited. The permittee shall not cause, suffer, allow, or permit the discharge of air pollutants which cause or contribute to an objectionable odor. [Rule 62-296.320(2), F.A.C.; Pinellas County Code, Section 58-178; AC52-189392] Comments: An upwind/downwind survey of the facility was conducted. The observed parameters were: Downwind odor detected- none; Wind direction – East Upwind odor detected-None 3. Prevention of Accidental Releases (Section 112(r) of CAA). A. The permittee shall submit its Risk Management Plan (RMP) to the Chemical Emergency Preparedness and Prevention Office (CEPPO) RMP Reporting Center when, and if, such requirement becomes applicable; and B. The permittee shall submit to the permitting authority Title V certification forms or a compliance schedule in accordance with Rule 62-213.440(2), F.A.C. [40 CFR 68] Comments: This facility submitted the RMP at the time of the original application and it is on file. 5. The "Statement of Compliance" required to be submitted to this office and the EPA shall be submitted at the same time as the Annual Operating Report. Note to Permittee: see Appendix TV-3, Nos. 23 and 51. [Rules 62-213.420(4), 62-213.440(3), and 62-4.070(3), F.A.C.] Comments: The 2006 SOC was submitted on 3/12/07. I informed Mr. Fairburn, that Bayfront has been required to re-submit the Annual Statement of Compliance (ASOC) for 2006 to the AQD. The ASOC re-submittal should be completed with option “C” checked, indicating a non-compliance with permit condition A.84, which will be processed as a Compliance Without Enforcement (CWOE). Resolution of the noncompliance will be achieved with the re-submittal of the ASOC and the 4 Quarterly Excess Emissions Reports for 2006. 8. Any reports, data notifications, certification, and requests required to be sent to the United States Environmental Protection Agency, Region 4, should be sent to: [Rule 62-4.070(3), F.A.C.] B.1. Capacity. A. The maximum natural gas usage rate is 12,000 ft.3/hr. (12.6 MMBTU/hr. based on 1050 BTU/ft.3). B. The maximum new No. 2 fuel oil usage rate is 87 gals./hr. (11.75 MMBTU/hr. base on 135,000 BTU/gal.). [Rules 62-4.160(2) and 62-210.200(PTE), F.A.C.] Comments: The EU operated at an average rate of 5,688 ft3 /hr. Total Natural Gas consumption was 31. 376 MM ft3 for the past 12 months from March 1st, 2006 to February 28th 2007. B.3. Hours of Operation. The boiler's hours of operation are not restricted, 8,760 hours/yr. Note, a boiler is considered in operation any time fuel is being fired. [Rule 62-4.160(2) and 62-210.200(PTE), F.A.C.] Comments: This Boiler operated 5,516 hrs in the past 12 months from March 1st, 2006 to February 28th 2007. Emission Limitations B.4. Visible emissions from the boiler shall not exceed 20% opacity except for one six-minute period per hour during which opacity shall not exceed 27%. [Rule 62-296.406(1), F.A.C.] Comments: The Boiler was not operating at the time of my visit. Test Method and Procedures {Permitting Note: Table 2-1, Summary of Compliance Requirements summarizes information for convenience purposes only. This table does not supercede any of the terms or conditions of this permit.} B.5. The boiler shall be tested for visible emissions within 60 days after the effective date of this permit and annually thereafter. In addition, if the most recent annual visible emissions test was conducted with the boiler fired with natural gas, then within 30 days of the boiler exceeding the 400th hour of using fuel oil shall conduct another visible emissions test when the boiler is fired with fuel oil. Annual visible emission tests shall be conducted during each federal fiscal year (October 1 - September 30). [Rule 62-297.310(7), F.A.C.] Comments: The last test performed on this Boiler yielded an Opacity of 0.0 %. B.6. Visible emission testing of the boiler shall be accomplished when the boiler is operating within 90 - 100% of the maximum allowable fuel usage rate as stipulated in Condition B.1. If it is impractical to test at this rate, the boiler may be tested at less than the maximum permitted capacity; in this case, subsequent operation of the boiler is limited to 110 percent of the tested fuel usage rate until a new test is conducted. Once the boiler is so limited, operation at a higher fuel usage is allowed for no more than 15 consecutive days for the purpose of additional compliance testing to regain the authority to operate at the permitted capacity. Testing at conditions which are not representative of normal operating conditions may invalidate the test. [Rules 62-297.310(2) and 62-4.070(3), F.A.C.] Comments: The Boiler operated at 9,600 ft3 /hr when tested on 9/19/06. B.9. The permittee shall notify the Air Compliance Section of PCDEM at least 15 days prior to the date on which each formal compliance test is to begin of the date, time, and place of each such test, and the test contact person who will be responsible for coordinating and having such test conducted for the owner. [Rule 62-297.310(7)(a)9, F.A.C.] Comments: The facility tested EU 002 on 9/19/06 for PM, HCl and CO. The facility gave more than 15 days prior notification to the AQD. Recordkeeping and Reporting B.10. The permittee shall comply with the following: A. Pursuant to 40 CFR 60.48c NSPS Subpart Dc (Standards of Performance for Small Industrial-Commercial-Institutional Steam Generating Units), the permittee is required to maintain daily records of the hours of operation and amount of natural gas combusted in the boiler. If the most recent visible emissions test was conducted within 90 - 100% of the maximum allowable natural gas usage rate and since none of the emission limits in Subpart Dc are applicable to the boiler when firing natural gas, it has been determined by the Department that keeping records for natural gas usage and hours of operation on a monthly rather than daily basis is adequate for the purpose of verifying the periods that only natural gas is burned in this boiler. These records shall be recorded in a permanent form suitable for inspection upon request and shall be retained for at least a 5 year period from the date of such recording. [Rule 62-204.800, F.A.C., and 40 CFR 60.48c(g) and (i) (Subpart Dc)] B. The permittee shall maintain a daily record of the hours of operation and quantity of fuel oil used in the boiler for each day of operation. If the most recent visible emission test was conducted using natural gas, a separate daily record documenting the hours of firing fuel oil, until the 400th hour, is required in order to comply with the testing requirements of Condition No. C.5. These records shall be recorded in a permanent form suitable for inspection upon request, and shall be retained for at least a 5 year period from the date of such recording. [Rule 62-204.800(7)(b)4., F.A.C., and 40 CFR 60.48c(g) & 60.48c(i) (Subpart Dc).] C. Ongoing compliance with the fuel oil's 0.05%, by weight, sulfur content limitation shall be demonstrated through either: - The fuel supplier documentation of fuel oil sulfur content for each shipment of oil delivered for use in the boiler per 40 CFR 60.48c(f). The records shall include a "fuel supplier certification" (40 CFR 60.48c(f)) consisting of the name of the oil supplier and a statement from the oil supplier that the oil complies with the specifications for fuel oil number 4, as defined by the American Society for Testing and Materials in ASTM D396-78, "Standard Specification for Fuel Oils"; or - Actual fuel oil analysis per 40 CFR 60.60c(d)(2). Fuel sampling and analysis shall be in accordance with 40 CFR 60 Appendix A, Method 19, Section 5.2.2 (Liquid Fossil Fuel). These records shall be recorded in a permanent form suitable for inspection upon request, and shall be retained for at least a 5 year period. [Rules 62-4.070(3), and 62-204.800, F.A.C., and 40 CFR 60.46c(e), 60.48c(e)(11), 60.48c(f) and 60.48c(i)] D. The permittee shall submit for the boiler quarterly reports of the fuel oil supplier sulfur content certification records required by Condition B.10.C. (above) for any calendar quarter during which fuel oil is fired. In addition to the above, the quarterly report shall include a certified statement signed by the facility's responsible official that the records of the fuel supplier certifications submitted represent all of the fuel combusted during the quarter. The quarterly reports shall be submitted to the Air Compliance Section of this office and the PCDEM within 30 days of the end of the quarter being reported. [Rule 62-204.800(7)(b)4., F.A.C., and 40 CFR 60.48c(e)(11) (Subpart Dc)] E. Monthly record the consecutive 12 month total of: - Hours of operation. 2. Quantity of natural gas used (fired), in million cubic feet. 3. Quantity of fuel oil used (fired), in gallons. [Rule 62-4.070(3), F.A.C.] Comments: The Boiler is fired exclusively on Natural Gas. Excess Emissions {Permitting Note: The Excess Emissions Rule at Rule 62-210.700, F.A.C., cannot vary any requirement of an Emissions Guideline, NSPS, or NESHAP.} B.11. At all times, including periods of startup, shutdown, and malfunction, owners and operators shall, to the extent practicable, maintain and operate any affected facility including associated air pollution control equipment in a manner consistent with good air pollution control practice for minimizing emissions. Determination of whether acceptable operating and maintenance procedures are being used will be based on information available to the Administrator which may include, but is not limited to, monitoring results, opacity observations, review of operating and maintenance procedures, and inspection of the source. [40 CFR 60.11(d)] Comments: There were no excess emissions for the reporting period. B.19. In case of excess emissions resulting from malfunctions, each owner or operator shall notify the Air Compliance Section of this office and the PCDEM in accordance with Rule 62-4.130, F.A.C. A full written report on the malfunctions shall be submitted in a quarterly report, if requested by the Department. [Rule 62-210.700(6), F.A.C.] Comments: There were no excess emissions for the reporting period |
|  |  |  | #### Valid Permit [Rule 62-210.300] |
|  |  |  | #### Changes to Facility/emission unit [Rule 62-210.300] Does the emission unit description above match what the facility is operating  Yes No Comments: |

|  |  | C. Other: |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Pollution Prevention Activities - P2 Handouts Provided: P2 Brochure; P2 Manual; P2 Checklist - Have any emissions reductions occurred Yes /  No Chemical Substitution; Equipment Changes; Process Changes Chemical/Material Reuse; On-site Recycling; Other: Comments: |  |  |  |  |  |  |  |
| Closing Conference: The facility was in compliance and mr. Fairburn was informed. |  |  |  |  |  |  |  |
| Inspector(s): Jose Rodriguez, Pinellas County, Air Quality Division |  |  |  |  |  |  |  |
| Signature(s): Date: |  |  |  |  |  |  | Date: |
|  | # ACCESS? |  |  | # EASIIR? |  |  |  |