| 1030443 75651 |  |
| --- | --- |
| FACILITY: Lorad Chemical Corporation | PERMIT ID: 1572 |
| Lorad Chemical | DISTRICT: Southwest |
| ADDRESS: 1200 19th Street North | CONTACT PHONE: |
| St. Petersburg, FL | 826-5511 |
| ARMS NO: 1030443 001 | PERMIT NO: | Expiration Date: 9/11/2011 Renewal Date: 7/13/2011 |
|  | 1030443-004-AO |  |
|  |  | Test Due Date: |
| EMISSION UNIT DESCRIPTION : Aqueous Reactions Room: Includes fluoride reactions conducted in a tube furnace, chloride purification, conducted in a reaction vessel, and aqueous precipitation reactions. Emission Controlled by Scrubber No. 1 |
| INSPECTION DATE: | ARMS INSPECTION TYPE: | COMPLIANCE STATUS: |
|  | November 4, 2010 |  |  | INS1 | ( | INS2 |  | INS3 |  | FUI | ( | IN |  | MNC |  | SNC |
| INSPECTION TYPE: | ( | Initial |  | Re-inspection |  | Complaint |  | Drive-by |  | Quarterly |
| ( | A. General Review: |
| 1. | Permit File Review |  | Yes |  | No |
|  | Comments: |  |  |  |  |
| 2. | Introduction and Entry |  | Yes |  | No |
|  | Comments: |  |  |  |  |
| 3. | Is the Responsible Official/Authorized Representative still: Alan Saunders? |  | Yes |  | No |
|  | Comments: The Responsible Official/Authorized Representative’s e-mail is: |
| 4. | Is the facility contact still: Alan Saunders? |  | Yes |  | No |
|  | Comments: The facility contact’s e-mail is: |

| IN | MNC | SNC | B. Specific Conditions: |
| --- | --- | --- | --- |
| ( ( ( ( ( ( ( ( ( ( ( ( ( ( ( ( ( ( |  |  | Inspection note: This renewal permit became effective on 09/11/2006 This permit or a copy thereof shall be kept at the work site of the permitted activity. [62-4.160 F.A.C. - General Condition 12.] Comments: The facility did did not have a copy of the permit on-site. Emissions And Operation Limitations 4. Production Limits - The production rate of inorganic chemicals from reactions that emit HCl, Cl2, HF, and/or H2S (i.e., the reactions controlled by the scrubbers) shall not exceed 30 kg/day (66 lb/day), daily average basis. [Rules 62-4.160(2) & 62-210.200(PTE), F.A.C.; 1030443-002-AC] Comments: 15 kg/day was the highest production total on May 11, 2010 5. General Pollutant Emission Limiting Standards - Objectionable Odor Prohibited - The permittee shall not cause, suffer, allow, or permit the discharge of air pollutants from this plant which cause or contribute to an objectionable odor. Objectionable odor is defined as “Any odor present in the outdoor atmosphere which by itself or in combination with other odors, is or may be harmful or injurious to human health or welfare, which unreasonably interferes with the comfortable use and enjoyment of life or property, or which creates a nuisance.” [Rules 62-296.320(2) and 62-210.200, Definitions (Objectionable Odor), F.A.C.; Pinellas County Code, Section 58-178] Comments: No objectionable odor detected 6. Circumvention of Control Device – The permittee shall not allow any person to circumvent any air pollution control device, or allow the emission of air pollutants without the applicable control device operating properly. All process reaction emissions shall be vented to the appropriate scrubber. [Rules 62-210.650, and 62-4.070(3), F.A.C.] Comments: No circumvention of control devices 7. Scrubber pH - Process reactions shall not be conducted unless the appropriate scrubber is operating at a minimum pH of 10.0. [Rule 62-4.070(3), F.A.C.; Response letter received March 1, 1999; 1030443-002-AC] Comments: Scrubber#1 ph=14 and Scrubber #2 ph=13 8. Scrubber Liquid Flow Rate - Process reactions shall not be conducted unless the appropriate scrubber is operating at minimum liquid flow rates of: Pre-scrubber - 3.7 gpm Lower Nozzle - 35 gpm Upper Nozzle - 35 gpm [Rule 62-4.070(3), F.A.C.; Response letter received March 1, 1999; 1030443-002-AC] Comments: Scrubber #1 Lower Nozzle – 37 gpm Upper Nozzle – 37 gpm Pre-Scrubber – 4 gpm Scrubber #2 Lower Nozzle -38 gpm Upper Nozzle – 40 gpm Pre-Scrubber – 5 gpm Monitoring Requirements 9. Monitoring Devices - In order to demonstrate compliance with Specific Condition Nos. 7 and 8, the permittee shall install, calibrate, operate, and maintain monitoring devices for the pre-scrubber, lower- and upper-nozzle liquid-flow rates and the scrubbing-liquid pH, in accordance with the vendor’s specifications. For each scrubber, the monitoring devices shall display the above flow rates and the scrubbing-liquid pH continuously by gauge or digital readout and be recorded at least once per operating day by manual recordkeeping or data logger. [Rule 62-4.070(3), F.A.C.] Comments: Inspection included checking the gauges. Gauges on both scrubbers were operating in compliance with vendor’s specifications. There were no problems with any of the bubble gauges during the compliance year 10. Special Compliance Tests - When the Department or Pinellas County Department of Environmental Management (PCDEM), after investigation, has good reason (such as complaints or questionable maintenance of control equipment) to believe that any applicable emission standard contained in a Department rule or in a permit issued pursuant to those rules is being violated, it shall require the owner or operator of the emissions unit to conduct compliance tests which identify the nature and quantity of pollutant emissions from the emissions unit and to provide a report on the results of said tests to the Air Compliance Sections of the Department’s Southwest District Office and the Air Quality Division of the PCDEM. [Rule 62-297.310(7)(b), F.A.C.] Comments: No special compliance test was necessary during the compliance year Recordkeeping And Reporting Requirements 11. Recordkeeping - In order to document compliance with the production limits of Specific Condition No. 4, and operating limits of Specific Condition No. 7 and 8, the permittee shall record, at a minimum, the following: Daily Production Records (each day of operation): Facility Name, Emission Unit No., Date. Total, daily production of inorganic chemicals from reactions controlled by scrubbers (lb or kg) Daily Scrubber Operations Records (at least once per day) Scrubbing liquid flow rates and pH for each scrubber (EU-001 & EU-002). Date and time of the measurements. Name of the person responsible for performing the measurements. MSDS Records Maintain records (MSD sheets, purchase orders, mass of all HAP-containing materials used, etc.) needed to estimate emissions. [Rules 62 4.070(3), F.A.C. and Pinellas County Code Section 58-90] Comments: A. Daily production records were reviewed. These records are hand recorded in a log book kept at the facility. B. Operational Daily Checks are hand recorded on a spreadsheet. A copy of the spreadsheet is attached to the compliance file C. MSDS and purchase order records were reviewed. 12. Records Retention - The records required by Specific Condition No. 11 shall be retained on file at the facility for at least five (5) year and shall be made available to the Department or the PCDEM upon request. [Rules 62 4.070(3), F.A.C. and Pinellas County Code Section 58-90] Comments: Records exist back to 2004 13. Operation and Maintenance (O&M) Plan – The scrubbers shall be operated and maintained in accordance with the Operation and Maintenance (O&M) Plan submitted to this office on February 21st, 2006, and as amended in accordance with response letter dated June 12th, 2006. The O&M plan may be revised with the approval of the PCDEM. The O&M Plan documentation logs shall be maintained for a minimum of five (5) years. At a minimum the O&M plan shall include: The operating parameters of the control device. Timetable for routine maintenance of the control device as specified by manufacturer. Timetable of routine periodic observations of pollution control device sufficient to ensure proper operation. A list of the type and quantity of the required spare parts for the pollution-control device which are stored on the premises of the permit applicant. A record log which will indicate, at a minimum: When maintenance was performed. What maintenance was performed. Who performed said maintenance and observations. Acceptable parameter ranges for each operational check. [Pinellas County Code, Section 58-128] Comments: The O&M plan meets the conditions a-e. There was no deviation or changes to O&M plan during the compliance year 14. O&M Plan Submittal – Within ninety (90) days of the effective date of this permit, the permittee shall submit a copy of the latest O&M Plan (as amended in accordance with Lorad Chemical Corporation’s response letter dated June 12th, 2006) along with blank copies of each scrubber log to the Air Permitting Section of the Department’s Southwest District Office with a copy to the Air Quality Division of the PCDEM. [Rule 62-4.070(3), F.A.C.] Comments: The facility submitted the O&M Plan within 90 days of the effective date of the permit. There were no changes to the O&M Plan during the compliance year 15. Plant Operation-Problems - If the permittee is temporarily unable to comply with any of the conditions of the permit due to breakdown of equipment or destruction by hazard of fire, wind or by other cause, the permittee shall immediately notify the Air Compliance Sections of the Department’s Southwest District Office and the Air Quality Division of the PCDEM. Notification shall include pertinent information as to the cause of the problem, and what steps are being taken to correct the problem and to prevent its recurrence, and where applicable, the owner's intent toward reconstruction of destroyed facilities. Such notification does not release the permittee from any liability for failure to comply with Department rules. [Rule 62-4.130, F.A.C.] Comments: There were no plant operation-problems during the compliance year 16. Definition “Immediately” - For purposes of notification to the Department pursuant to Rule 62-4.130, F.A.C., Plant Operation-Problems, “immediately” shall mean the same day, if during a workday (i.e., 8:00 a.m. - 5:00 p.m.), or the first business day after the incident, excluding weekends and holidays. [Rule 62-4.070(3), F.A.C.] Comments: There were no plant operation-problems reported during the compliance year Operation Permit Renewal 17. Operation Permit Renewal Application - A completed application to renew the operation permit shall be submitted to the Air Permitting Section of the Department’s Southwest District Office of the Department, with a copy to the Air Quality Division of the PCDEM, no later than 60 days prior to the expiration date of this permit… [Rules 62-4.090, 62-4.070(3) & 62-210.300(2), F.A.C.] Comments: The facility will need to complete its renewal 60 days prior to September 11, 2011 |
| ( |  |  | Valid Permit [Rule 62-210.300] |
|  |  |  | Changes to Facility/emission unit [Rule 62-210.300] Does the emission unit description above match what the facility is operating (Number of emission units or points, model number and serial number, etc.) Yes No Comments: |
| ( | C. Other: |
| Pollution Prevention Activities P2 Handouts Provided: P2 Brochure; P2 Manual; P2 Checklist Have any emissions reductions occurred Yes / No Chemical Substitution; Equipment Changes; Process Changes Chemical/Material Reuse; On-site Recycling; Other: Comments: No pollution prevention activities during the compliance year |
| Closing Conference: |
| Inspector(s): Jeffrey Morris, Pinellas County, Air Quality Division |
| Signature(s): Date: | Date: |
| ACCESS? | ( | ARMS? | ( |